## Refrigerant & Oil Charge
Refrigerant and Oil Charge Calculation
| version D(2) |  | fill in blue cells |  |  | 114X6003 : OP-UPAC015COP04E
2024.03.08
| Refrigerant charge | [6 empty] | Oil charge addition
Pipe inventory that connect the last evaporator of group 1
[7 empty] | Refrigerant Charge | Suction pipe diam |  | Length | Oil addition | Oil addition
[7 empty] | kg | inches | mm | m | cc/m | cc
| Condensing Unit Baseline Charge | [5 empty] | 10.2 | 3/4'' | 19.05 | 0 | 16 | 0
[8 empty] | 5/8'' | 15.875 | 0 | 11 | 0
| Liquid Line Diam |  | pipe thickness | Internal volume | Liquid Line Length | Average density | Refrigerant Charge | 1/2'' | 12.7 | 0 | 7 | 0
| inches | mm | mm | L/m | m | kg/L | kg | 3/8'' | 9.525 | 0 | 5 | 0
| 3/4'' | 19.05 | 1.4 | 0.20739 | 5 | 1.085 | 1.1251 | 1/4'' | 6.35 | 0 | 3 | 0
| 5/8'' | 15.875 | 1.2 | 0.14261 | 5 |  | 0.77365
| 1/2'' | 12.7 | 1.2 | 0.083323 | 0 |  | 0 | Pipe inventory that connect the last evaporator of group 2
| 1/2'' | 12.7 | 1 | 0.08992 | 0 |  | 0 | Suction pip |  | Length | Oil addition | Oil addition
| 3/8'' | 9.525 | 1 | 0.044474 | 0 |  | 0 | inches | mm | m | cc/m | cc
| 3/8'' | 9.525 | 0.8 | 0.049327 | 0 |  | 0 | 3/4'' | 19.05 | 0 | 16 | 0
| 1/4'' | 6.35 | 1 | 0.014862 | 0 |  | 0 | 5/8'' | 15.875 | 0 | 11 | 0
| 1/4'' | 6.35 | 0.8 | 0.017721 | 0 |  | 0 | 1/2'' | 12.7 | 0 | 7 | 0
| 1/4'' | 6.35 | 0.5 | 0.02248 | 0 |  | 0 | 3/8'' | 9.525 | 0 | 5 | 0
| Total Liquid Line Charge | [5 empty] | 1.8988 | 1/4'' | 6.35 | 0 | 3 | 0
| Evaporator (max 8 Evaporators) |  |  | Internal volume | Evaporating Temperature | Average density | Refrigerant Charge | Total Oil addition |  |  | cc | 0
| Id |  |  | L | degC | kg/L | kg | equivalent 3/4'' Length |  |  | m | 0
| 1 |  |  | 30 | -35 | 0.037691 | 1.1307 | Max Oil addition |  |  | cc | 950
| 2 |  |  | 0 |  |  | 0 | If calculation is less than 640 cc, it is not necessary to add oil.
| 3 |  |  | 0 |  |  | 0
| 4 |  |  | 0 |  |  | 0
| 5 |  |  | 0 |  |  | 0
| 6 |  |  | 0 |  |  | 0
| 7 |  |  | 0 |  |  | 0 | Oil to add to system |  |  | cc | 0
| 8 |  |  | 0 |  |  | 0 | System oil charge after addition |  |  | cc | 1830
| Total charge required by evaporator | [5 empty] | 1.1307
| Equivalent pipe 1/2'' length |  |  |  |  | m | 19.4619
| System Charge Lmit |  |  |  |  | kg | 17.5988
Total charge charge should never exceed the above limit. This is to protect the condensing unit of being overcharged. Overfilling the system may risk of liquid return to compressor through bypass valve when running. Overfilling the system may risk in pressure increase and release of refrigerant through the receiver relief valve during standstill.
WARNING : Ensure that the minimum load demand coming from the cold rooms/display cabinets shall be greater than 50% of the cooling capacity of the condensing unit at lowest speed.
| Total system Charge = CDU Baseline Charge + Liquid Line + Evaporator charge |  |  |  |  | kg | 13.2295 | For evaporating Temperatures between |  | Range of evaporating temperature | Minimum capacity allowed
[10 empty] | From -35 to -45°C | 1,9 kW
| Warning(s): | [8 empty] | From -20 to -34°C | 3,0 kW
[10 empty] | From -5 to -19°C | 4,1 kW
[10 empty] | From -45 to +5°C | 5,1 kW
WARNING : During the minimal running configuration, (At compressor lowest speed), you can use defrost time or modulating thermostat control.
Total Evaporator Internal Volume is > 27 L, contact Danfoss to get final validation
Ex.: on low temperature application, if minimum load is 2,81kW (At compressor lowest speed 30%), then minimum demand from cold rooms/display cabinets should be maintain around 1.4kW.
Legal Disclaimer
These calculation tools are based on theoritical facts and may vary from field installation.
Have the unit installed by your agent or specialized contractor. Electrical work needs to be done by a qualified electrical work contractor. Improper installation made by yourself may cause electric shock or fire.
The unit must be loaded in accordance with the rules of art.
During commissioning, do not run the unit undercharged (80% of charge calculated) for more than 10 minutes, you may have the risk to reach a very high discharge temperature and to limit the reliability of the compressor.
Failure to follow the refrigerant and oil charging procedure will invalidate the warranty.
Do not leave the system running if oil return has not been detected and confirmed within one hour (1h).(look inside guideline or instruction manual)
If total internal evaporator volume is more than 27L, Danfoss must be contacted to get final validation.
Ensure all parts of the circuit have enough fluid velocity to ensure oil return to the compressor on all operating conditions.
Check list needs to be done to validate Danfoss warranty at the time of commissioning
Danfoss might change this file without further notice depending on its customer experience

## evap CDU charge (hidden)
Evaporating Temperature | CDU charge | evap charge
degC | kg | kg/L
-35 | 10.2 | 0.037691