## Sheet1
Danfoss IPS 8
Calculation of savings
The penalty for an increased condensing temperature depends on the compressor type and operating condition
The numbers stated below is an average found from calculations of several compressors in several operating conditions
1 °C higher condensing temperature leads to:
3% lower COP
3% higher power consumption
1% lower cooling capacity
A condenser with proper function will have a very limited subcooling, usually in the range of 1 to 1.5°C
While incorrect piping of the condenser can influence the subcooling, assuming that the piping is correct, a significantly larger subcooling signifies air in the condenser.
The increase in condensing temperature can only be estimated from the subcooling, but 40 to 50% of the subcooling above 1K is a realistic value.
Input fields
|  | Power consumption of high stage compressors | 1000 | kW
|  | Running time per year | 5000 | hrs
|  | Measured subcooling | 4 | K
|  | Cost of energy | 0.05 | EUR/kWh
Output fields
|  | Annual power consumption of high stage compressors (with air) | 5000000 | kWh
|  | Annual power expenses | 250000 | EUR
|  | Estimated increase in condensing temperature | 1.5 | K
|  | Estimated increase in power consumption | 6.06%
|  | Annual extra energy concumption due to air | 302980.2941 | kWh
|  | Annual savings with air purger | 15100 | EUR