## Cold room foundation
Cold Store. Frost heave prevention system
Evaluative calculation |  |  |  | Informational data (for more information see Application manual)
Cells with gray color - for data entry
Object data
| Voltage | 220 | V
| Cold room air temperature | -20 | °C
| Thickness of the insulation | 10 | cm
| Coefficient of thermal conductivity of insulation, λ | 0.035 | W/(m·°C)
| Safety factor | 1.3 | recommended 1,3
| Heated area | 100 | m2
| System Calculation for main system | [6 empty] | Calculated cable length | 250 | m
| Heat loss for chosen cold room air temp. with safety factor | 11.375 | W/m2
| Min. installed specific output | 15 | W/m2
Cables
| DEVIflex 10T, 230 V | 9.1493 | W/m |  |  | 230 | 10 | 120 | 2 | 1220
| Choose Center-to-Center distance (C-C) between cables | 40 | cm
| Calculated specific output | 22.8733 | W/m2
| DEVIflex 10T 1220W 230V 120m | 140F1229 | 2 pcs.
| Total cable length | 240 | m
| Calculated total output | 2195.8412 | W
Thermostats
| DEVIreg™ 330 (-10 ... +10°C) | 140F1070 | 2 pcs.
Accessories
| DEVIfast™ Metal 25 m In box | 19808236 | 8 pcs. |  |  | 8 pcs.
System Calculation for reserve system
Cables
| DEVIflex 10T, 230 V | 9.1493 | W/m
| Center-to-Center distance (C-C) between reserve cables | 40 | cm
| Calculated cable length | 250 | m
| DEVIflex 10T 1220W 230V 120m | 140F1229 | 2 pcs.
| Total cable length | 240 | m
| Calculated total output | 2195.8412 | W
Thermostats
| DEVIreg™ 330 (-10 ... +10°C) | 140F1070 | 2 pcs.
| Center-to-Center distance (C-C) between main and reserve systems | 2,5...5 | cm
Settings for control system
| Thermostat temp. setting for main system | + 5 | °C
| Thermostat temp. setting for reserve system | + 3 | °C
Important to know
Note 1. One thermostat per heating cable should be installed.
Note 2. Max. resistive load for DEVIreg 330 is 16 A (3680 W).
Note 3. If a voltage of 220 V, use the coefficient 0,915 for cable output.
Note 4. DEVIfast/ECfast is recommended to use for cable fixing (fixings step 2,5 cm).
| Note 5. Installing the thermostat is recommended. |  |  |  | Technical support: EH@danfoss.com
Note on C9: Drop-down list
Note on B20: Drop-down list
Note on C21: Drop-down list
Note on B27: Drop-down list
Note on B29: Drop-down list

## Cold room doors
Cold Store. Protection against condensation on floors. Freeze protection of doors and gates.
Evaluative calculation |  |  |  | Informational data (for more information see Application manual)
| Cells with gray color - for data entry |  |  |  | Protection against condensation on floors.
Object data
| Voltage | 230 | V
| Cold room air temperature | -30 | °C
| Door width | 0.9 | m
| Door height | 2 | m
System Calculation for floor
| Min. installed specific output | 240 | W/m2
Cables
| DEVIflex 18T, 230 V | 18 | W/m |  |  | 230 | 18
| Choose Center-to-Center distance (C-C) between cables | 5 | cm
| Calculated specific output | 360 | W/m2
| Temperature of floor surface, tfl | 11.3793 | °C
| Inside heated area, S1 | 1.8 | m2 |  |  |  |  | Calculated cable length for S1 | 36 | m
| Outside heated area, S2 | 1.8 | m2 |  |  |  |  | Calculated cable length for S2 | 36 | m
| DEVIflex 18T 310W 230V 17.5m | 140F1401 | 2 pcs. |  |  | 17.5 | 2 | 310
| DEVIflex 18T 310W 230V 17.5m | 140F1401 | 2 pcs.
| Total cable length | 70 | m
| Calculated total output | 1260 | W
Thermostats
| DEVIreg™ 330 (-10 ... +10°C) | 140F1070 | 1 pcs.
| DEVIreg™ 330 (-10 ... +10°C) | 140F1070 | 1 pcs. |  | Freeze protection of doors and gates.
Accessories
| DEVIfast™ Metal 25 m In box | 19808236 | 1 pcs.
System Calculation for door frame
Cables
| DEVIsnow 30T, 230 V | 30 | W/m
| Choose Center-to-Center distance (C-C) between cables | 7.5 | cm
| Calculated specific output | 400 | W/m2
| Cable lines in the door frame | 2 | units |  |  |  |  | Calculated cable length | 11.6 | m
| DEVIsnow 30T 300W 230V 10m | 89846000 | 1 pcs. |  |  | 10 | 1 | 300
| Total cable length | 10 | m
| Calculated total output | 300 | W
Thermostat
| DEVIreg™ 330 (+5 ... +45°C) | 140F1072 | 1 pcs.
Accessories
| Tape aluminium 38 mm x 50 m | 19805076 | 1 pcs.
Important to know
Note 1. One thermostat per heating cable should be installed.
Note 2. Max. resistive load for DEVIreg 330 is 16 A (3680 W).
Note 3. If a voltage of 220 V, use the coefficient 0,915 for cable output.
Note 4. DEVIfast/ECfast is recommended to use for cable fixing (fixings step 2,5 cm).
| Note 5. Installing the thermostat is recommended. |  |  |  | Technical support: EH@danfoss.com
Note on C9: Drop-down list
Note on B17: Drop-down list
Note on C18: Drop-down list
Note on B28: Drop-down list
Note on B29: Drop-down list
Note on B31: Drop-down list
Note on B35: Drop-down list
Note on C36: Drop-down list
Note on B43: Drop-down list
Note on B45: Drop-down list

## Cables Base (hidden)
|  | 3 |  | 2 |  | 1
|  | 83.3333 |  | 125 |  | 250 | m |  |  | Product name |  | NWP, Euro
DEVIflex 6T, 230 V | DEVIflex 6T 500W 230V 80m | 80 |  | 115 |  | 200 |  |  |  | DEVIflex 6T | 0 | 0
|  | 240 | 0.96001 | 230 | 0.92002 |  | 30 | 0.80003 |  | DEVIflex 6T 180W 230V 30m | 140F1200 | 47.2513 | 30 | 30 | 180 | 180
|  |  | DEVIflex 6T 500W 230V 80m |  | DEVIflex 6T 720W 230V 115m |  | 40 | DEVIflex 6T 1260W 230V 200m | 140F1214 | DEVIflex 6T 250W 230V 40m | 140F1201 | 57.5741 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.19997 |  | DEVIflex 6T 310W 230V 50m | 140F1202 | 56.8685 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | DEVIflex 6T 345W 230V 60m | 140F1203 | 67.5677 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | DEVIflex 6T 415W 230V 70m | 140F1204 | 74.3959 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | DEVIflex 6T 500W 230V 80m | 140F1205 | 90.3704 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | DEVIflex 6T 540W 230V 90m | 140F1206 | 89.0582 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | DEVIflex 6T 635W 230V 100m | 140F1207 | 99.4569 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | DEVIflex 6T 720W 230V 115m | 140F1208 | 106.49 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | DEVIflex 6T 770W 230V 129m | 140F1209 | 119.4648 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | DEVIflex 6T 870W 230V 140m | 140F1210 | 131.6305 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | DEVIflex 6T 915W 230V 160m | 140F1211 | 163.8981 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | DEVIflex 6T 1095W 230V 180m | 140F1212 | 183.8546 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | DEVIflex 6T 1160W 230V 190m | 140F1213 | 173.5159 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | DEVIflex 6T 1260W 230V 200m | 140F1214 | 188.2218 | 200 | 200 | 1260 | 1260
DEVIflex 10T, 230 V | DEVIflex 10T 1220W 230V 120m | 80 |  | 120 |  | 210 | 0 |  |  | DEVIflex 10T | 0 | 0 |  | 0 |  | 0
|  | 240 | 0.96001 | 240 | 0.96002 |  | 2 | 0.84003 |  | DEVIflex 10T 20W 230V 2m | 140F1215 | 31.3109 | 2 | 2 | 20 | 20
|  |  | DEVIflex 10T 790W 230V 80m |  | DEVIflex 10T 1220W 230V 120m |  | 4 | DEVIflex 10T 2050W 230V 210m | 140F1234 | DEVIflex 10T 40W 230V 4m | 140F1216 | 33.2887 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.15997 |  | DEVIflex 10T 60W 230V 6m | 140F1217 | 35.3357 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | DEVIflex 10T 80W 230V 8m | 140F1218 | 37.0131 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | DEVIflex 10T 100W 230V 10m | 140F1219 | 36.6142 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | DEVIflex 10T 135W 230V 15m | 140F1407 | 42.4905 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | DEVIflex 10T 205W 230V 20m | 140F1220 | 43.4206 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | DEVIflex 10T 240W 230V 25m | 140F1408 | 50.0213 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | DEVIflex 10T 290W 230V 30m | 140F1221 | 52.2615 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | DEVIflex 10T 365W 230V 35m | 140F1409 | 57.4915 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | DEVIflex 10T 390W 230V 40m | 140F1222 | 61.3884 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | DEVIflex 10T 505W 230V 50m | 140F1223 | 73.761 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | DEVIflex 10T 600W 230V 60m | 140F1224 | 83.1366 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | DEVIflex 10T 695W 230V 70m | 140F1225 | 92.4731 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | DEVIflex 10T 790W 230V 80m | 140F1226 | 104.2358 | 80 | 80 | 790 | 790
[7 empty] | 90 |  |  | DEVIflex 10T 920W 230V 90m | 140F1227 | 109.1824 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | DEVIflex 10T 990W 230V 100m | 140F1228 | 123.8087 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | DEVIflex 10T 1220W 230V 120m | 140F1229 | 137.0674 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | DEVIflex 10T 1410W 230V 140m | 140F1230 | 161.5301 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | DEVIflex 10T 1575W 230V 160m | 140F1231 | 168.7374 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | DEVIflex 10T 1760W 230V 180m | 140F1232 | 177.3665 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | DEVIflex 10T 1990W 230V 200m | 140F1233 | 214.8776 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | DEVIflex 10T 2050W 230V 210m | 140F1234 | 206.4709 | 210 | 210 | 2050 | 2050
DEVIflex 18T, 230 V | DEVIflex 18T 1485W 230V 82m | 82 |  | 118 |  | 170 | 0 |  |  | DEVIflex 18T | 0 | 0 |  | 0 |  | 0
|  | 246 | 0.98401 | 236 | 0.94402 |  | 7.3 | 0.68003 |  | DEVIflex 18T 130W 230V 7.3m | 140F1235 | 29.9305 | 7.3 | 7.3 | 130 | 130
|  |  | DEVIflex 18T 1485W 230V 82m |  | DEVIflex 18T 2135W 230V 118m |  | 10 | DEVIflex 18T 3050W 230V 170m | 140F1402 | DEVIflex 18T 180W 230V 10m | 140F1236 | 32.7963 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.31997 |  | DEVIflex 18T 230W 230V 12.8m | 140F1400 | 31.6809 | 2.8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | DEVIflex 18T 270W 230V 15m | 140F1237 | 37.6402 | 15 | 15 | 270 | 270
[7 empty] | 17.5 |  |  | DEVIflex 18T 310W 230V 17.5m | 140F1401 | 35.4159 | 17.5 | 17.5 | 310 | 310
[7 empty] | 22 |  |  | DEVIflex 18T 395W 230V 22m | 140F1238 | 42.8216 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | DEVIflex 18T 535W 230V 29m | 140F1239 | 52.2865 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | DEVIflex 18T 615W 230V 34m | 140F1240 | 47.3052 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | DEVIflex 18T 680W 230V 37m | 140F1241 | 59.3457 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | DEVIflex 18T 820W 230V 44m | 140F1242 | 62.4281 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | DEVIflex 18T 935W 230V 52m | 140F1243 | 72.9463 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | DEVIflex 18T 1005W 230V 54m | 140F1410 | 68.9071 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | DEVIflex 18T 1075W 230V 59m | 140F1244 | 71.7261 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | DEVIflex 18T 1220W 230V 68m | 140F1245 | 85.3535 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | DEVIflex 18T 1340W 230V 74m | 140F1246 | 95.2464 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | DEVIflex 18T 1485W 230V 82m | 140F1247 | 94.8881 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | DEVIflex 18T 1625W 230V 90m | 140F1248 | 101.7635 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | DEVIflex 18T 1880W 230V 105m | 140F1249 | 124.4419 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | DEVIflex 18T 2135W 230V 118m | 140F1250 | 127.4416 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | DEVIflex 18T 2420W 230V 131m | 140F1251 | 147.1973 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | DEVIflex 18T 2775W 230V 155m | 140F1252 | 138.063 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | DEVIflex 18T 3050W 230V 170m | 140F1402 | 163.7246 | 170 | 170 | 3050 | 3050
DEVIsafe 20T, 230 V | DEVIsafe 20T 2360W 230V 118m | 76 |  | 118 |  | 194 |  |  |  | DEVIsafe 20T | 0 | 0 |  | 0 |  | 0
|  | 228 | 0.91201 | 236 | 0.94402 |  | 6 | 0.77603 |  | DEVIsafe 20T 125W 230V 6m | 140F1273 | 28.9254 | 6 | 6 | 125 | 125
|  |  | DEVIsafe 20T 1545W 230V 76m |  | DEVIsafe 20T 2360W 230V 118m |  | 12 | DEVIsafe 20T 3895W 230V 194m | 140F1288 | DEVIsafe 20T 250W 230V 12m | 140F1274 | 39.2108 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.22397 |  | DEVIsafe 20T 335W 230V 17m | 140F1275 | 44.1423 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | DEVIsafe 20T 505W 230V 25m | 140F1276 | 51.718 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsafe 20T 675W 230V 33m | 140F1277 | 57.804 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | DEVIsafe 20T 830W 230V 42m | 140F1278 | 66.0327 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | DEVIsafe 20T 1000W 230V 50m | 140F1279 | 77.6812 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsafe 20T 1200W 230V 60m | 140F1280 | 89.9506 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | DEVIsafe 20T 1370W 230V 68m | 140F1281 | 97.1499 | 68 | 68 | 1370 | 1370
[7 empty] | 76 |  |  | DEVIsafe 20T 1545W 230V 76m | 140F1199 | 102.8038 | 76 | 76 | 1545 | 1545
[7 empty] | 85 |  |  | DEVIsafe 20T 1700W 230V 85m | 140F1282 | 109.215 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | DEVIsafe 20T 2040W 230V 101m | 140F1283 | 125.7509 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | DEVIsafe 20T 2360W 230V 118m | 140F1284 | 138.3392 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | DEVIsafe 20T 2685W 230V 135m | 140F1285 | 144.806 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | DEVIsafe 20T 3025W 230V 152m | 140F1286 | 157.0882 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | DEVIsafe 20T 3385W 230V 170m | 140F1287 | 174.0406 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | DEVIsafe 20T 3895W 230V 194m | 140F1288 | 190.3484 | 194 | 194 | 3895 | 3895
DEVIsnow 20T, 230 V | DEVIsnow 20T 2421W 230V 115m | 70 |  | 115 |  | 195 |  |  |  | DEVIsnow 20T, 230 V | 0 |  |  | 0 |  | 0
|  | 210 | 0.84001 | 230 | 0.92002 |  | 6 | 0.78003 |  | DEVIsnow 20T 125W 230V 6m | 140F1116 |  | 6 | 6 | 125 | 125
|  |  | DEVIsnow 20T 1333W 230V 70m |  | DEVIsnow 20T 2421W 230V 115m |  | 12 | DEVIsnow 20T 3875W 230V 195m | 83902111 | DEVIsnow 20T 250W 230V 12m | 83902100 |  | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.21997 |  | DEVIsnow 20T 332W 230V 17m | 140F1117 |  | 17 | 17 | 332 | 332
[7 empty] | 25 |  |  | DEVIsnow 20T 505W 230V 25m | 83902101 |  | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsnow 20T 677W 230V 33m | 140F1118 |  | 33 | 33 | 677 | 677
[7 empty] | 40 |  |  | DEVIsnow 20T 855W 230V 40m | 83902102 |  | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | DEVIsnow 20T 1000W 230V 50m | 83902103 |  | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsnow 20T 1200W 230V 60m | 83902104 |  | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | DEVIsnow 20T 1333W 230V 70m | 83902105 |  | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | DEVIsnow 20T 1695W 230V 85m | 83902106 |  | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | DEVIsnow 20T 2060W 230V 100m | 83902107 |  | 100 | 100 | 2060 | 2060
[7 empty] | 115 |  |  | DEVIsnow 20T 2421W 230V 115m | 140F1119 |  | 115 | 115 | 2421 | 2421
[7 empty] | 135 |  |  | DEVIsnow 20T 2685W 230V 135m | 83902108 |  | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | DEVIsnow 20T 3066W 230V 150m | 83902109 |  | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | DEVIsnow 20T 3382W 230V 170m | 83902110 |  | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | DEVIsnow 20T 3875W 230V 195m | 83902111 |  | 195 | 195 | 3875 | 3875
DEVIsnow 30T, 230 V | DEVIsnow 30T 3680W 230V 125m | 78 |  | 125 |  | 140 | 0 |  |  | DEVIsnow 30T, 230 V | 0 | 0 |  | 0 |  | 0
|  | 234 | 0.93601 | 250 | 1 |  | 5 | 0.56003 |  | DEVIsnow 30T 150W 230V 5m | 89845995 | 27.7051 | 5 | 5 | 150 | 150
|  |  | DEVIsnow 30T 2340W 230V 78m |  | DEVIsnow 30T 3680W 230V 125m |  | 10 | DEVIsnow 30T 4110W 230V 140m | 89846032 | DEVIsnow 30T 300W 230V 10m | 89846000 | 47.6576 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.43997 |  | DEVIsnow 30T 400W 230V 14m | 89846002 | 53.3626 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | DEVIsnow 30T 630W 230V 20m | 89846004 | 61.8816 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | DEVIsnow 30T 830W 230V 27m | 89846006 | 71.4505 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | DEVIsnow 30T 1020W 230V 34m | 89846008 | 82.4261 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | DEVIsnow 30T 1250W 230V 40m | 89846010 | 90.9761 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | DEVIsnow 30T 1350W 230V 45m | 89846012 | 97.6812 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | DEVIsnow 30T 1440W 230V 50m | 89846014 | 106.9097 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | DEVIsnow 30T 1700W 230V 55m | 89846016 | 116.9281 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | DEVIsnow 30T 1860W 230V 63m | 89846018 | 128.1624 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | DEVIsnow 30T 2060W 230V 70m | 89846020 | 133.5726 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | DEVIsnow 30T 2340W 230V 78m | 89846022 | 145.3033 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | DEVIsnow 30T 2420W 230V 85m | 89846024 | 150.4317 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | DEVIsnow 30T 2930W 230V 95m | 89846026 | 160.1027 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | DEVIsnow 30T 3290W 230V 110m | 89846028 | 179.2554 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | DEVIsnow 30T 3680W 230V 125m | 89846030 | 188.7066 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | DEVIsnow 30T 4110W 230V 140m | 89846032 | 192.178 | 140 | 140 | 4110 | 4110
DEVIcomfort 10T, 230 V | DEVIcomfort 10T 800W 230V 81m with double adhesive tape | 81 |  | 100 |  | 170 | 0 |  |  | Set DEVIcomfort 10T W/double adhesive tape | 0 | 0 |  | 0 |  | 0
|  | 243 | 0.97201 | 200 | 0.80002 |  | 10 | 0.68003 |  | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 87101700 | 37.1175 | 10 | 10 | 100 | 100
|  |  | DEVIcomfort 10T 800W 230V 81m with double adhesive tape |  | DEVIcomfort 10T 1000W 230V 100m with double adhesive tape |  | 20 | DEVIcomfort 10T 1700W 230V 170m with double adhesive tape | 87101728 | DEVIcomfort 10T 200W 230V 20m with double adhesive tape | 87101702 | 39.3455 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.31997 |  | DEVIcomfort 10T 300W 230V 28m with double adhesive tape | 87101706 | 42.4788 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m with double adhesive tape | 87101708 | 55.8652 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m with double adhesive tape | 87101710 | 58.5378 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m with double adhesive tape | 87101712 | 71.8987 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m with double adhesive tape | 87101714 | 69.4793 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m with double adhesive tape | 87101716 | 86.3431 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m with double adhesive tape | 87101718 | 90.337 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m with double adhesive tape | 87101720 | 96.8938 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m with double adhesive tape | 87101722 | 102.8547 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m with double adhesive tape | 87101724 | 112.4678 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m with double adhesive tape | 87101728 | 139.6788 | 170 | 170 | 1700 | 1700
| DEVIcomfort 10T 800W 230V 81m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 81 |  | 100 |  | 170 |  |  |  | Set DEVIcomfort 10T W/Flexpipe and endcap | 0 | 0 |  |  |  | 0
|  | 243 | 0.97201 | 200 | 0.80002 |  | 10 | 0.68003 |  | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101100 | 57.557 | 10 | 10 | 100 | 100
|  |  | DEVIcomfort 10T 800W 230V 81m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m |  | DEVIcomfort 10T 1000W 230V 100m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m |  | 20 | DEVIcomfort 10T 1700W 230V 170m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101124 | DEVIcomfort 10T 200W 230V 20m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101102 | 56.2081 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.31997 |  | DEVIcomfort 10T 300W 230V 28m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101104 | 68.2614 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101106 | 84.2502 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101108 | 100.2324 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101110 | 111.7354 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101112 | 129.5072 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101114 | 138.2771 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101116 | 148.0345 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101118 | 167.7854 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101120 | 198.9273 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101122 | 213.6489 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101124 | 246.4735 | 170 | 170 | 1700 | 1700
DEVIbasic 10S, 230 V | DEVIbasic 10S 1245W 230V 125m | 77 |  | 125 |  | 230 |  |  |  | DEVIbasic 10S | 0 | 0
|  | 231 | 0.92401 | 250 | 1 |  | 21 | 0.92003 |  | DEVIbasic 10S 202W 230V 21m | 84001500 | 42.0258 | 21 | 21 | 202 | 202
|  |  | DEVIbasic 10S 763W 230V 77m |  | DEVIbasic 10S 1245W 230V 125m |  | 26 | DEVIbasic 10S 2300W 230V 230m | 84001585 | DEVIbasic 10S 268W 230V 26m | 84001505 | 31.1078 | 26 | 26 | 268 | 268
[7 empty] | 30 | 0.07997 |  | DEVIbasic 10S 299W 230V 30m | 84001510 | 41.096 | 30 | 30 | 299 | 299
[7 empty] | 37 |  |  | DEVIbasic 10S 376W 230V 37m | 84001515 | 36.0663 | 37 | 37 | 376 | 376
[7 empty] | 46 |  |  | DEVIbasic 10S 446W 230V 46m | 84001520 | 39.8957 | 46 | 46 | 446 | 446
[7 empty] | 50 |  |  | DEVIbasic 10S 501W 230V 50m | 84001525 | 40.4031 | 50 | 50 | 501 | 501
[7 empty] | 58 |  |  | DEVIbasic 10S 570W 230V 58m | 84001530 | 41.3 | 58 | 58 | 570 | 570
[7 empty] | 66 |  |  | DEVIbasic 10S 668W 230V 66m | 84001535 | 44.1354 | 66 | 66 | 668 | 668
[7 empty] | 77 |  |  | DEVIbasic 10S 763W 230V 77m | 84001540 | 50.942 | 77 | 77 | 763 | 763
[7 empty] | 90 |  |  | DEVIbasic 10S 904W 230V 90m | 84001545 | 48.2002 | 90 | 90 | 904 | 904
[7 empty] | 103 |  |  | DEVIbasic 10S 1027W 230V 103m | 84001550 | 53.7508 | 103 | 103 | 1027 | 1027
[7 empty] | 114 |  |  | DEVIbasic 10S 1133W 230V 114m | 84001555 | 59.6308 | 114 | 114 | 1133 | 1133
[7 empty] | 125 |  |  | DEVIbasic 10S 1245W 230V 125m | 84001560 | 73.5661 | 125 | 125 | 1245 | 1245
[7 empty] | 140 |  |  | DEVIbasic 10S 1400W 230V 140m | 84001565 | 76.5857 | 140 | 140 | 1400 | 1400
[7 empty] | 159 |  |  | DEVIbasic 10S 1584W 230V 159m | 84001570 | 84.2231 | 159 | 159 | 1584 | 1584
[7 empty] | 170 |  |  | DEVIbasic 10S 1707W 230V 170m | 84001575 | 106.6948 | 170 | 170 | 1707 | 1707
[7 empty] | 188 |  |  | DEVIbasic 10S 1876W 230V 188m | 84001580 | 108.3834 | 188 | 188 | 1876 | 1876
[7 empty] | 230 |  |  | DEVIbasic 10S 2300W 230V 230m | 84001585 | 179.3887 | 230 | 230 | 2300 | 2300
[7 empty] | 275 |  |  | DEVIbasic 10S 2741W 230V 275m | 84001590 | 237.7555 | 275 | 275 | 2741 | 2741
[7 empty] | 325 |  |  | DEVIbasic 10S 3245W 230V 325m | 84001595 | 253.4445 | 325 | 325 | 3245 | 3245
[7 empty] | 407 |  |  | DEVIbasic 10S 4069W 230V 407m | 84001600 | 322.5794 | 407 | 407 | 4069 | 4069
DEVIbasic 20S, 230 V | DEVIbasic 20S 4575W 400V 229m | 74 |  | 110 |  | 229 |  |  |  | DEVIbasic 20S, 230 V | 0 | 0
|  | 222 | 0.88801 | 220 | 0.88002 |  | 9 | 0.91603 |  | DEVIbasic 20S 170W 230V 9m | 140F0260 | 21.6338 | 9 | 9 | 170 | 170
|  |  | DEVIbasic 20S 1465W 230V 74m |  | DEVIbasic 20S 2215W 230V 110m |  | 14 | DEVIbasic 20S 4575W 400V 229m | 140F0235 | DEVIbasic 20S 260W 230V 14m | 140F0215 | 24.4171 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.08397 |  | DEVIbasic 20S 375W 230V 18m | 140F0216 | 26.8774 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | DEVIbasic 20S 520W 230V 26m | 140F0217 | 32.1521 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | DEVIbasic 20S 640W 230V 32m | 140F0218 | 37.123 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | DEVIbasic 20S 800W 230V 39m | 140F0219 | 41.5959 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | DEVIbasic 20S 1070W 230V 53m | 140F0220 | 51.5364 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | DEVIbasic 20S 1260W 230V 63m | 140F0221 | 59.717 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | DEVIbasic 20S 1465W 230V 74m | 140F0222 | 71.7707 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | DEVIbasic 20S 1820W 230V 91m | 140F0223 | 85.0183 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | DEVIbasic 20S 2215W 230V 110m | 140F0224 | 102.2243 | 110 | 110 | 2215 | 2215
[7 empty] | 131 |  |  | DEVIbasic 20S 2640W 230V 131m | 140F0225 | 117.6106 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | DEVIbasic 20S 3170W 230V 159m | 140F0226 | 137.5381 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | DEVIbasic 20S 3855W 230V 192m | 140F0227 | 160.6359 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | DEVIbasic 20S 4565W 230V 228m | 140F0228 | 154.2219 | 228 | 228 | 4565 | 4565
[7 empty] | 56 |  |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 | 67.4779 | 56 | 56 | 1100 | 1100
[7 empty] | 69 |  |  | DEVIbasic 20S 1375W 400V 69m | 140F0230 | 74.5087 | 69 | 69 | 1375 | 1375
[7 empty] | 93 |  |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 | 121.6736 | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 | 150.2169 | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 | 169.5973 | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 | 160.3213 | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 | 187.3359 | 229 | 229 | 4575 | 4575
DEVIbasic 20S, 400 V | DEVIbasic 20S 4575W 400V 229m | 69 |  | 93 |  | 229 |  |  |  | DEVIbasic 20S, 400 V |  |  |  | 0
| 0.91603 | 207 | 0.82801 | 186 | 0.74402 |  | 56 | 0.91603 |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 |  | 56 | 56 | 1100 | 1100
|  |  | DEVIbasic 20S 1375W 400V 69m |  | DEVIbasic 20S 1850W 400V 93m |  | 69 | DEVIbasic 20S 4575W 400V 229m | 140F0235 | DEVIbasic 20S 1375W 400V 69m | 140F0230 |  | 69 | 69 | 1375 | 1375
[7 empty] | 93 | 0.08397 |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 |  | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 |  | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 |  | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 |  | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 |  | 229 | 229 | 4575 | 4575
ECflex 6T, 230 V | ECflex 6T 500W 230V 80m | 80 |  | 115 |  | 200 |  |  |  | ECflex 6T | 0 | 0 |  | 0
|  | 240 | 0.96001 | 230 | 0.92002 |  | 30 | 0.80003 |  | ECflex 6T 180W 230V 30m | 088L6436 | 56.452 | 30 | 30 | 180 | 180
|  |  | ECflex 6T 500W 230V 80m |  | ECflex 6T 720W 230V 115m |  | 40 | ECflex 6T 1260W 230V 200m | 088L6450 | ECflex 6T 250W 230V 40m | 088L6437 | 61.78 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.19997 |  | ECflex 6T 310W 230V 50m | 088L6438 | 0 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | ECflex 6T 345W 230V 60m | 088L6439 | 0 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | ECflex 6T 415W 230V 70m | 088L6440 | 95.73 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | ECflex 6T 500W 230V 80m | 088L6441 | 84.31 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | ECflex 6T 540W 230V 90m | 088L6442 | 0 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | ECflex 6T 635W 230V 100m | 088L6443 | 0 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | ECflex 6T 720W 230V 115m | 088L6444 | 115.97 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | ECflex 6T 770W 230V 129m | 088L6445 | 135.21 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | ECflex 6T 870W 230V 140m | 088L6446 | 0 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | ECflex 6T 915W 230V 160m | 088L6447 | 0 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | ECflex 6T 1095W 230V 180m | 088L6448 | 0 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | ECflex 6T 1160W 230V 190m | 088L6449 | 0 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | ECflex 6T 1260W 230V 200m | 088L6450 | 134.45 | 200 | 200 | 1260 | 1260
ECflex 10T, 230 V | ECflex 10T 1220W 230V 120m | 80 |  | 120 |  | 210 |  |  |  | ECflex 10T | 0 | 0 |  | 0
|  | 240 | 0.96001 | 240 | 0.96002 |  | 2 | 0.84003 |  | ECflex 10T 20W 230V 2m | 088L6021 | 0 | 2 | 2 | 20 | 20
|  |  | ECflex 10T 795W 230V 80m |  | ECflex 10T 1220W 230V 120m |  | 4 | ECflex 10T 2050W 230V 210m | 088L6080 | ECflex 10T 40W 230V 4m | 088L6022 | 23.66 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.15997 |  | ECflex 10T 60W 230V 6m | 088L6023 | 23.675 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | ECflex 10T 80W 230V 8m | 088L6024 | 38.848 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | ECflex 10T 100W 230V 10m | 088L6025 | 35.7395 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | ECflex 10T 135W 230V 15m | 088L6074 | 33.3757 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | ECflex 10T 205W 230V 20m | 088L6026 | 55.0854 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | ECflex 10T 240W 230V 25m | 088L6075 | 31.1582 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | ECflex 10T 290W 230V 30m | 088L6027 | 64.9289 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | ECflex 10T 365W 230V 35m | 088L6076 | 39.4572 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | ECflex 10T 390W 230V 40m | 088L6028 | 72.2422 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | ECflex 10T 505W 230V 50m | 088L6029 | 81.8063 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | ECflex 10T 600W 230V 60m | 088L6030 | 101.6101 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | ECflex 10T 695W 230V 70m | 088L6031 | 79.21 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | ECflex 10T 795W 230V 80m | 088L6032 | 112.065 | 80 | 80 | 795 | 795
[7 empty] | 90 |  |  | ECflex 10T 920W 230V 90m | 088L6073 | 105.5445 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | ECflex 10T 990W 230V 100m | 088L6034 | 124.7212 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | ECflex 10T 1220W 230V 120m | 088L6035 | 155.1798 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | ECflex 10T 1410W 230V 140m | 088L6036 | 164.6128 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | ECflex 10T 1575W 230V 160m | 088L6077 | 128.7611 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | ECflex 10T 1760W 230V 180m | 088L6078 | 132.6395 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | ECflex 10T 1990W 230V 200m | 088L6079 | 163.5142 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | ECflex 10T 2050W 230V 210m | 088L6080 | 170.1106 | 210 | 210 | 2050 | 2050
ECflex 18T, 230 V | ECflex 18T 1485W 230V 82m | 82 |  | 118 |  | 170 |  |  |  | ECflex 18T | 0 | 0 |  | 0
|  | 246 | 0.98401 | 236 | 0.94402 |  | 7.3 | 0.68003 |  | ECflex 18T 130W 230V 7,3m | 088L6037 | 29.5982 | 7,3 | 7.3 | 130 | 130
|  |  | ECflex 18T 1485W 230V 82m |  | ECflex 18T 2135W 230V 118m |  | 10 | ECflex 18T 3050W 230V 170m | 088L6084 | ECflex 18T 180W 230V 10m | 088L6038 | 37.1244 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.31997 |  | ECflex 18T 230W 230V 12,8m | 088L6081 | 0 | 2,8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | ECflex 18T 270W 230V 15m | 088L6039 | 39.7327 | 15 | 15 | 270 | 270
[7 empty] | 7.5 |  |  | ECflex 18T 310W 230V 17,5m | 088L6082 | 45.79 | 7,5 | 7.5 | 310 | 310
[7 empty] | 22 |  |  | ECflex 18T 395W 230V 22m | 088L6040 | 43.2868 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | ECflex 18T 535W 230V 29m | 088L6041 | 51.0825 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | ECflex 18T 615W 230V 34m | 088L6042 | 56.3231 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | ECflex 18T 680W 230V 37m | 088L6043 | 61.1988 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | ECflex 18T 820W 230V 44m | 088L6044 | 66.18 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | ECflex 18T 935W 230V 52m | 088L6045 | 75.4182 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | ECflex 18T 1005W 230V 54m | 088L6083 | 115.765 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | ECflex 18T 1075W 230V 59m | 088L6046 | 76.8697 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | ECflex 18T 1220W 230V 68m | 088L6047 | 84.6495 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | ECflex 18T 1340W 230V 74m | 088L6048 | 89.1979 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | ECflex 18T 1485W 230V 82m | 088L6049 | 99.5225 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | ECflex 18T 1625W 230V 90m | 088L6050 | 101.0678 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | ECflex 18T 1880W 230V 105m | 088L6051 | 109.4646 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | ECflex 18T 2135W 230V 118m | 088L6052 | 117.1417 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | ECflex 18T 2420W 230V 131m | 088L6053 | 126.0686 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | ECflex 18T 2775W 230V 155m | 088L6054 | 143.8278 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | ECflex 18T 3050W 230V 170m | 088L6084 | 160.0119 | 170 | 170 | 3050 | 3050
ECflex 20T, 230 V | ECflex 20T 2530W 230V 125m | 78 |  | 125 |  | 148 | 0 |  |  | ECflex 20T | 0 | 0 |  | 0
|  | 234 | 0.93601 | 250 | 1 |  | 7.1 | 0.59203 |  | ECflex 20T 140W 230V 7,1m | 088L6055 | 30.0769 | 7,1 | 7.1 | 140 | 140
|  |  | ECflex 20T 1565W 230V 78m |  | ECflex 20T 2530W 230V 125m |  | 10 | ECflex 20T 2905W 230V 148m | 088L6072 | ECflex 20T 195W 230V 10m | 088L6056 | 34.7379 | 10 | 10 | 195 | 195
[7 empty] | 16.5 | 0.40797 |  | ECflex 20T 330W 230V 16,5m | 088L6057 | 40.2383 | 16,5 | 16.5 | 330 | 330
[7 empty] | 21 |  |  | ECflex 20T 415W 230V 21m | 088L6058 | 39.123 | 21 | 21 | 415 | 415
[7 empty] | 28 |  |  | ECflex 20T 555W 230V 28m | 088L6059 | 41.1882 | 28 | 28 | 555 | 555
[7 empty] | 32 |  |  | ECflex 20T 650W 230V 32m | 088L6060 | 40.9284 | 32 | 32 | 650 | 650
[7 empty] | 36 |  |  | ECflex 20T 700W 230V 36m | 088L6061 | 48.0644 | 36 | 36 | 700 | 700
[7 empty] | 43 |  |  | ECflex 20T 835W 230V 43m | 088L6062 | 53.9827 | 43 | 43 | 835 | 835
[7 empty] | 50 |  |  | ECflex 20T 970W 230V 50m | 088L6063 | 62.8224 | 50 | 50 | 970 | 970
[7 empty] | 56 |  |  | ECflex 20T 1130W 230V 56m | 088L6064 | 63.0011 | 56 | 56 | 1130 | 1130
[7 empty] | 65 |  |  | ECflex 20T 1275W 230V 65m | 088L6065 | 60.3244 | 65 | 65 | 1275 | 1275
[7 empty] | 70 |  |  | ECflex 20T 1415W 230V 70m | 088L6066 | 69.6247 | 70 | 70 | 1415 | 1415
[7 empty] | 78 |  |  | ECflex 20T 1565W 230V 78m | 088L6067 | 85.983 | 78 | 78 | 1565 | 1565
[7 empty] | 86 |  |  | ECflex 20T 1700W 230V 86m | 088L6068 | 88.4146 | 86 | 86 | 1700 | 1700
[7 empty] | 100 |  |  | ECflex 20T 1975W 230V 100m | 088L6069 | 91.5054 | 100 | 100 | 1975 | 1975
[7 empty] | 112 |  |  | ECflex 20T 2250W 230V 112m | 088L6070 | 94.6579 | 112 | 112 | 2250 | 2250
[7 empty] | 125 |  |  | ECflex 20T 2530W 230V 125m | 088L6071 | 106.6561 | 125 | 125 | 2530 | 2530
[7 empty] | 148 |  |  | ECflex 20T 2905W 230V 148m | 088L6072 | 104.4955 | 148 | 148 | 2905 | 2905
ECbasic 20S, 230 V | ECbasic 20S 4565W 230V 228m | 74 |  | 110 |  | 228 | 0 |  |  | ECbasic 20S, 230 V | 0 | 0 |  | 0
|  | 222 | 0.88801 | 220 | 0.88002 |  | 9 | 0.91203 |  | ECbasic 20S 170W 230V 9m | 088L2130 | 28.7912 | 9 | 9 | 170 | 170
|  |  | ECbasic 20S 1465W 230V 74m |  | ECbasic 20S 2025W 230V 110m |  | 14 | ECbasic 20S 4565W 230V 228m | 088L2144 | ECbasic 20S 260W 230V 14m | 088L2131 | 33.2947 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.08797 |  | ECbasic 20S 375W 230V 18m | 088L2132 | 34.8516 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | ECbasic 20S 520W 230V 26m | 088L2133 | 38.1866 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | ECbasic 20S 640W 230V 32m | 088L2134 | 38.3272 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | ECbasic 20S 800W 230V 39m | 088L2135 | 46.3013 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | ECbasic 20S 1070W 230V 53m | 088L2136 | 55.6788 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | ECbasic 20S 1260W 230V 63m | 088L2137 | 63.4345 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | ECbasic 20S 1465W 230V 74m | 088L2138 | 68.8052 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | ECbasic 20S 1820W 230V 91m | 088L2139 | 79.3664 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | ECbasic 20S 2025W 230V 110m | 088L2140 | 93.4831 | 110 | 110 | 2025 | 2025
[7 empty] | 131 |  |  | ECbasic 20S 2640W 230V 131m | 088L2141 | 100.3531 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | ECbasic 20S 3170W 230V 159m | 088L2142 | 118.2952 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | ECbasic 20S 3855W 230V 192m | 088L2143 | 182.0267 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | ECbasic 20S 4565W 230V 228m | 088L2144 | 192.4472 | 228 | 228 | 4565 | 4565
ECsafe 20T, 230 V | ECsafe 20T 2360W 230V 118m | 68 |  | 118 |  | 194 | 0 |  |  | ECsafe 20T, 230 V | 0 | 0 |  | 0
|  | 204 | 0.81601 | 236 | 0.94402 |  | 6 | 0.77603 |  | ECsafe 20T 125W 230V 6m | 088L2170 | 40.081 | 6 | 6 | 125 | 125
|  |  | ECsafe 20T 1370W 230V 68m |  | ECsafe 20T 2360W 230V 118m |  | 12 | ECsafe 20T 3895W 230V 194m | 088L2185 | ECsafe 20T 250W 230V 12m | 088L2171 | 31.9684 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.22397 |  | ECsafe 20T 335W 230V 17m | 088L2172 | 68.228 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | ECsafe 20T 505W 230V 25m | 088L2173 | 43.6554 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | ECsafe 20T 675W 230V 33m | 088L2174 | 76.9596 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | ECsafe 20T 830W 230V 42m | 088L2175 | 74.052 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | ECsafe 20T 1000W 230V 50m | 088L2176 | 91.4092 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsafe 20T 1200W 230V 60m | 088L2177 | 97.1683 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | ECsafe 20T 1370W 230V 68m | 088L2178 | 141.2821 | 68 | 68 | 1370 | 1370
[7 empty] | 85 |  |  | ECsafe 20T 1700W 230V 85m | 088L2179 | 108.6337 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | ECsafe 20T 2040W 230V 101m | 088L2180 | 151.7474 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | ECsafe 20T 2360W 230V 118m | 088L2181 | 170.2478 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | ECsafe 20T 2685W 230V 135m | 088L2182 | 143.5807 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | ECsafe 20T 3025W 230V 152m | 088L2183 | 212.4829 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | ECsafe 20T 3385W 230V 170m | 088L2184 | 173.5106 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | ECsafe 20T 3895W 230V 194m | 088L2185 | 197.8234 | 194 | 194 | 3895 | 3895
ECsnow 20T, 230 V | ECsnow 20T 1333W 230V 70m | 70 |  | 100 |  | 195 | 0 |  |  | ECsnow 20T, 230 V | 0 | 0 |  | 0
|  | 210 | 0.84001 | 200 | 0.80002 |  | 12 | 0.78003 |  | ECsnow 20T 250W 230V 12m | 088L0470 | 50.0246 | 12 | 12 | 250 | 250
|  |  | ECsnow 20T 1333W 230V 70m |  | ECsnow 20T 2060W 230V 100m |  | 25 | ECsnow 20T 3875W 230V 195m | 088L0481 | ECsnow 20T 505W 230V 25m | 088L0471 | 75.545 | 25 | 25 | 505 | 505
[7 empty] | 40 | 0.21997 |  | ECsnow 20T 855W 230V 40m | 088L0472 | 70.278 | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | ECsnow 20T 1000W 230V 50m | 088L0473 | 102.9437 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsnow 20T 1200W 230V 60m | 088L0474 | 98.592 | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | ECsnow 20T 1333W 230V 70m | 088L0475 | 112.234 | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | ECsnow 20T 1695W 230V 85m | 088L0476 | 126.2978 | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | ECsnow 20T 2060W 230V 100m | 088L0477 | 140.0643 | 100 | 100 | 2060 | 2060
[7 empty] | 135 |  |  | ECsnow 20T 2685W 230V 135m | 088L0478 | 237.331 | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | ECsnow 20T 3066W 230V 150m | 088L0479 | 225.2117 | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | ECsnow 20T 3382W 230V 170m | 088L0480 | 240.192 | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | ECsnow 20T 3875W 230V 195m | 088L0481 | 268.514 | 195 | 195 | 3875 | 3875
ECsnow 20T, 400 V | ECsnow 20T 1463W 400V 72m | 72 |  | 105 |  | 205 | 0 |  |  | ECsnow 20T, 400 V | 0 | 0 |  | 0
|  | 216 | 0.86401 | 210 | 0.84002 |  | 21 | 0.82003 |  | ECsnow 20T 433W 400V 21m | 088L0482 | 0 | 21 | 21 | 433 | 433
|  |  | ECsnow 20T 1463W 400V 72m |  | ECsnow 20T 2073W 400V 105m |  | 30 | ECsnow 20T 4108W 400V 205m | 088L0492 | ECsnow 20T 570W 400V 30m | 088L0483 | 127.31 | 30 | 30 | 570 | 570
[7 empty] | 43 | 0.17997 |  | ECsnow 20T 888W 400V 43m | 088L0484 | 0 | 43 | 43 | 888 | 888
[7 empty] | 58 |  |  | ECsnow 20T 1165W 400V 58m | 088L0485 | 149.93 | 58 | 58 | 1165 | 1165
[7 empty] | 72 |  |  | ECsnow 20T 1463W 400V 72m | 088L0486 | 173.05 | 72 | 72 | 1463 | 1463
[7 empty] | 85 |  |  | ECsnow 20T 1780W 400V 85m | 088L0487 | 0 | 85 | 85 | 1780 | 1780
[7 empty] | 105 |  |  | ECsnow 20T 2073W 400V 105m | 088L0488 | 0 | 105 | 105 | 2073 | 2073
[7 empty] | 135 |  |  | ECsnow 20T 2628W 400V 135m | 088L0489 | 261.5 | 135 | 135 | 2628 | 2628
[7 empty] | 150 |  |  | ECsnow 20T 2905W 400V 150m | 088L0490 | 0 | 150 | 150 | 2905 | 2905
[7 empty] | 170 |  |  | ECsnow 20T 3245W 400V 170m | 088L0491 | 0 | 170 | 170 | 3245 | 3245
[7 empty] | 205 |  |  | ECsnow 20T 4108W 400V 205m | 088L0492 | 565.7643 | 205 | 205 | 4108 | 4108
ECsnow 30T, 230 V | ECsnow 30T 3680W 230V 125m | 78 |  | 125 |  | 140 | 0 |  |  | ECsnow 30T, 230 V | 0 | 0 |  | 0
|  | 234 | 0.93601 | 250 | 1 |  | 5 | 0.56003 |  | ECsnow 30T 150W 230V 5m | 088L0230 | 40.71 | 5 | 5 | 150 | 150
|  |  | ECsnow 30T 2340W 230V 78m |  | ECsnow 30T 3680W 230V 125m |  | 10 | ECsnow 30T 4110W 230V 140m | 088L0248 | ECsnow 30T 300W 230V 10m | 088L0232 | 43.6665 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.43997 |  | ECsnow 30T 400W 230V 14m | 088L0233 | 67.3094 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | ECsnow 30T 630W 230V 20m | 088L0234 | 59.9004 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | ECsnow 30T 830W 230V 27m | 088L0235 | 67.2721 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | ECsnow 30T 1020W 230V 34m | 088L0236 | 71.2763 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | ECsnow 30T 1250W 230V 40m | 088L0237 | 77.9237 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | ECsnow 30T 1350W 230V 45m | 088L0238 | 90.352 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | ECsnow 30T 1440W 230V 50m | 088L0239 | 98.2883 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | ECsnow 30T 1700W 230V 55m | 088L0240 | 111.0086 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | ECsnow 30T 1860W 230V 63m | 088L0241 | 177.5437 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | ECsnow 30T 2060W 230V 70m | 088L0242 | 126.05 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | ECsnow 30T 2340W 230V 78m | 088L0243 | 137.5029 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | ECsnow 30T 2420W 230V 85m | 088L0244 | 145.1914 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | ECsnow 30T 2930W 230V 95m | 088L0245 | 169.1264 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | ECsnow 30T 3290W 230V 110m | 088L0246 | 170.9941 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | ECsnow 30T 3680W 230V 125m | 088L0247 | 219.1243 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | ECsnow 30T 4110W 230V 140m | 088L0248 | 228.6538 | 140 | 140 | 4110 | 4110
ECsnow 30T, 400 V | ECsnow 30T 3225W 400V 110m | 70 |  | 110 |  | 215 | 0 |  |  | ECsnow 30T, 400 V | 0 | 0 |  | 0
|  | 210 | 0.84001 | 220 | 0.88002 |  | 8.5 | 0.86003 |  | ECsnow 30T 267W 400V 8,5m | 088L0231 | 0 | 8,5 | 8.5 | 267 | 267
|  |  | ECsnow 30T 2160W 400V 70m |  | ECsnow 30T 3225W 400V 110m |  | 17.5 | ECsnow 30T 6470W 400V 215m | 088L0137 | ECsnow 30T 520W 400V 17,5m | 088L0130 | 130.16 | 17,5 | 17.5 | 520 | 520
[7 empty] | 35 | 0.13997 |  | ECsnow 30T 1090W 400V 35m | 088L0131 | 167.13 | 35 | 35 | 1090 | 1090
[7 empty] | 70 |  |  | ECsnow 30T 2160W 400V 70m | 088L0132 | 0 | 70 | 70 | 2160 | 2160
[7 empty] | 110 |  |  | ECsnow 30T 3225W 400V 110m | 088L0133 | 287.0967 | 110 | 110 | 3225 | 3225
[7 empty] | 145 |  |  | ECsnow 30T 4295W 400V 145m | 088L0134 | 325.2089 | 145 | 145 | 4295 | 4295
[7 empty] | 170 |  |  | ECsnow 30T 4955W 400V 170m | 088L0135 | 377.2227 | 170 | 170 | 4955 | 4955
[7 empty] | 190 |  |  | ECsnow 30T 5770W 400V 190m | 088L0136 | 432.585 | 190 | 190 | 5770 | 5770
[7 empty] | 215 |  |  | ECsnow 30T 6470W 400V 215m | 088L0137 | 493.1996 | 215 | 215 | 6470 | 6470
ECfreeze 7,5T, 400 V | ECfreeze 7,5T 241m 400V 1810W | 71 |  | 118 |  | 241 | 0 |  |  | ECfreeze 7,5T, 400 V | 0 | 0 |  | 0
|  | 213 | 0.85201 | 236 | 0.94402 |  | 35 | 0.96403 |  | ECfreeze 7,5T 35m 400V 260W | 088L6300 | 70.62 | 35 | 35 | 35 | 35
|  |  | ECfreeze 7,5T 71m 400V 540W |  | ECfreeze 7,5T 118m 400V 890W |  | 48 | ECfreeze 7,5T 241m 400V 1810W | 088L6307 | ECfreeze 7,5T 48m 400V 355W | 088L6301 | 94.07 | 48 | 48 | 48 | 48
[7 empty] | 71 | 0.03597 |  | ECfreeze 7,5T 71m 400V 540W | 088L6302 | 136.47 | 71 | 71 | 71 | 71
[7 empty] | 118 |  |  | ECfreeze 7,5T 118m 400V 890W | 088L6303 | 214.8767 | 118 | 118 | 118 | 118
[7 empty] | 142 |  |  | ECfreeze 7,5T 142m 400V 1065W | 088L6304 | 0 | 142 | 142 | 142 | 142
[7 empty] | 170 |  |  | ECfreeze 7,5T 170m 400V 1280W | 088L6305 | 278.04 | 170 | 170 | 170 | 170
[7 empty] | 217 |  |  | ECfreeze 7,5T 217m 400V 1635W | 088L6306 | 311.015 | 217 | 217 | 217 | 217
[7 empty] | 241 |  |  | ECfreeze 7,5T 241m 400V 1810W | 088L6307 | 469.2575 | 241 | 241 | 241 | 241
[7 empty] | 288 |  |  | ECfreeze 7,5T 288m 400V 2160W | 088L6308 | 401.76 | 288 | 288 | 288 | 288
[7 empty] | 382 |  |  | ECfreeze 7,5T 382m 400V 2870W | 088L6309 | 602.0573 | 382 | 382 | 382 | 382
[7 empty] | 431 |  |  | ECfreeze 7,5T 431m 400V 3230W | 088L6310 | 685.628 | 431 | 431 | 431 | 431
[7 empty] | 482 |  |  | ECfreeze 7,5T 482m 400V 3610W | 088L6311 | 669.5915 | 482 | 482 | 482 | 482
[7 empty] | 552 |  |  | ECfreeze 7,5T 552m 400V 4140W | 088L6312 | 859.0133 | 552 | 552 | 552 | 552
DEVIinline 17T, 230 V | DEVIinline 17T 2100w 230V 122.4m | 72.7 |  | 122.4 |  | 197 |  |  |  | DEVIinline 17T | 0 | 0
|  | 218.1 | 0.87241 | 244.8 | 0.97922 |  | 8.9 | 0.78803 |  | DEVIinline 17T 150w 230V 8.9m | 140F0670 | 22.6336 | 8.9 | 8.9 | 150 | 150
|  |  | DEVIinline 17T 1250w 230V 72.7m |  | DEVIinline 17T 2100w 230V 122.4m |  | 13.8 | DEVIinline 17T 3356w 230V 197m | 140F0688 | DEVIinline 17T 220w 230V 13.8m | 140F0671 | 29.4637 | 13.8 | 13.8 | 220 | 220
[7 empty] | 18.5 | 0.21197 |  | DEVIinline 17T 300w 230V 18.5m | 140F0672 | 35.2289 | 18.5 | 18.5 | 300 | 300
[7 empty] | 24.8 |  |  | DEVIinline 17T 400w 230V 24.8m | 140F0673 | 39.1685 | 24.8 | 24.8 | 400 | 400
[7 empty] | 31 |  |  | DEVIinline 17T 500w 230V 31m | 140F0674 | 41.6024 | 31 | 31 | 500 | 500
[7 empty] | 34.7 |  |  | DEVIinline 17T 600w 230V 34.7m | 140F0675 | 50.1831 | 34.7 | 34.7 | 600 | 600
[7 empty] | 40.6 |  |  | DEVIinline 17T 700w 230V 40.6m | 140F0676 | 51.75 | 40.6 | 40.6 | 700 | 700
[7 empty] | 49.4 |  |  | DEVIinline 17T 850w 230V 49.4m | 140F0677 | 60.8962 | 49.4 | 49.4 | 850 | 850
[7 empty] | 52 |  |  | DEVIinline 17T 884w 230V 52m | 140F0678 | 63.0429 | 52 | 52 | 884 | 884
[7 empty] | 58.1 |  |  | DEVIinline 17T 1000w 230V 58.1m | 140F0679 | 66.9593 | 58.1 | 58.1 | 1000 | 1000
[7 empty] | 68 |  |  | DEVIinline 17T 1156w 230V 68m | 140F0680 | 77.2147 | 68 | 68 | 1156 | 1156
[7 empty] | 72.7 |  |  | DEVIinline 17T 1250w 230V 72.7m | 140F0681 | 87.9433 | 72.7 | 72.7 | 1250 | 1250
[7 empty] | 87.3 |  |  | DEVIinline 17T 1500w 230V 87.3m | 140F0682 | 90.8188 | 87.3 | 87.3 | 1500 | 1500
[7 empty] | 99 |  |  | DEVIinline 17T 1700w 230V 99m | 140F0683 | 111.5161 | 99 | 99 | 1700 | 1700
[7 empty] | 110.7 |  |  | DEVIinline 17T 1900w 230V 110.7m | 140F0684 | 112.746 | 110.7 | 110.7 | 1900 | 1900
[7 empty] | 122.4 |  |  | DEVIinline 17T 2100w 230V 122.4m | 140F0685 | 118.1148 | 122.4 | 122.4 | 2100 | 2100
[7 empty] | 134.1 |  |  | DEVIinline 17T 2300w 230V 134.1m | 140F0686 | 122.5696 | 134.1 | 134.1 | 2300 | 2300
[7 empty] | 151.6 |  |  | DEVIinline 17T 2600w 230V 151.6m | 140F0687 | 133.7841 | 151.6 | 151.6 | 2600 | 2600
[7 empty] | 197 |  |  | DEVIinline 17T 3356w 230V 197m | 140F0688 | 167.0509 | 197 | 197 | 3356 | 3356

## Cables Floor Doors (hidden)
|  | 3 |  | 2 |  | 1
|  | 12 |  | 18 |  | 36 | m |  |  | Product name |  | NWP, Euro
DEVIflex 6T, 230 V | DEVIflex 6T 180W 230V 30m | 0 |  | 0 |  | 30 |  |  |  | DEVIflex 6T | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 30 | 0.83336 |  | DEVIflex 6T 180W 230V 30m | 140F1200 | 47.2513 | 30 | 30 | 180 | 180
|  |  | #N/A |  | #N/A |  | 40 | DEVIflex 6T 180W 230V 30m | 140F1200 | DEVIflex 6T 250W 230V 40m | 140F1201 | 57.5741 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.16664 |  | DEVIflex 6T 310W 230V 50m | 140F1202 | 56.8685 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | DEVIflex 6T 345W 230V 60m | 140F1203 | 67.5677 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | DEVIflex 6T 415W 230V 70m | 140F1204 | 74.3959 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | DEVIflex 6T 500W 230V 80m | 140F1205 | 90.3704 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | DEVIflex 6T 540W 230V 90m | 140F1206 | 89.0582 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | DEVIflex 6T 635W 230V 100m | 140F1207 | 99.4569 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | DEVIflex 6T 720W 230V 115m | 140F1208 | 106.49 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | DEVIflex 6T 770W 230V 129m | 140F1209 | 119.4648 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | DEVIflex 6T 870W 230V 140m | 140F1210 | 131.6305 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | DEVIflex 6T 915W 230V 160m | 140F1211 | 163.8981 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | DEVIflex 6T 1095W 230V 180m | 140F1212 | 183.8546 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | DEVIflex 6T 1160W 230V 190m | 140F1213 | 173.5159 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | DEVIflex 6T 1260W 230V 200m | 140F1214 | 188.2218 | 200 | 200 | 1260 | 1260
DEVIflex 10T, 230 V | DEVIflex 10T 365W 230V 35m | 10 |  | 15 |  | 35 | 0 |  |  | DEVIflex 10T | 0 | 0 |  | 0 |  | 0
|  | 30 | 0.83334 | 30 | 0.83335 |  | 2 | 0.97225 |  | DEVIflex 10T 20W 230V 2m | 140F1215 | 31.3109 | 2 | 2 | 20 | 20
|  |  | DEVIflex 10T 100W 230V 10m |  | DEVIflex 10T 135W 230V 15m |  | 4 | DEVIflex 10T 365W 230V 35m | 140F1409 | DEVIflex 10T 40W 230V 4m | 140F1216 | 33.2887 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.027748 |  | DEVIflex 10T 60W 230V 6m | 140F1217 | 35.3357 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | DEVIflex 10T 80W 230V 8m | 140F1218 | 37.0131 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | DEVIflex 10T 100W 230V 10m | 140F1219 | 36.6142 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | DEVIflex 10T 135W 230V 15m | 140F1407 | 42.4905 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | DEVIflex 10T 205W 230V 20m | 140F1220 | 43.4206 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | DEVIflex 10T 240W 230V 25m | 140F1408 | 50.0213 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | DEVIflex 10T 290W 230V 30m | 140F1221 | 52.2615 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | DEVIflex 10T 365W 230V 35m | 140F1409 | 57.4915 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | DEVIflex 10T 390W 230V 40m | 140F1222 | 61.3884 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | DEVIflex 10T 505W 230V 50m | 140F1223 | 73.761 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | DEVIflex 10T 600W 230V 60m | 140F1224 | 83.1366 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | DEVIflex 10T 695W 230V 70m | 140F1225 | 92.4731 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | DEVIflex 10T 790W 230V 80m | 140F1226 | 104.2358 | 80 | 80 | 790 | 790
[7 empty] | 90 |  |  | DEVIflex 10T 920W 230V 90m | 140F1227 | 109.1824 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | DEVIflex 10T 990W 230V 100m | 140F1228 | 123.8087 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | DEVIflex 10T 1220W 230V 120m | 140F1229 | 137.0674 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | DEVIflex 10T 1410W 230V 140m | 140F1230 | 161.5301 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | DEVIflex 10T 1575W 230V 160m | 140F1231 | 168.7374 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | DEVIflex 10T 1760W 230V 180m | 140F1232 | 177.3665 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | DEVIflex 10T 1990W 230V 200m | 140F1233 | 214.8776 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | DEVIflex 10T 2050W 230V 210m | 140F1234 | 206.4709 | 210 | 210 | 2050 | 2050
DEVIflex 18T, 230 V | DEVIflex 18T 310W 230V 17.5m | 10 |  | 17.5 |  | 34 | 0 |  |  | DEVIflex 18T | 0 | 0 |  | 0 |  | 0
|  | 30 | 0.83334 | 35 | 0.97224 |  | 7.3 | 0.94447 |  | DEVIflex 18T 130W 230V 7.3m | 140F1235 | 29.9305 | 7.3 | 7.3 | 130 | 130
|  |  | DEVIflex 18T 180W 230V 10m |  | DEVIflex 18T 310W 230V 17.5m |  | 10 | DEVIflex 18T 615W 230V 34m | 140F1240 | DEVIflex 18T 180W 230V 10m | 140F1236 | 32.7963 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.055526 |  | DEVIflex 18T 230W 230V 12.8m | 140F1400 | 31.6809 | 2.8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | DEVIflex 18T 270W 230V 15m | 140F1237 | 37.6402 | 15 | 15 | 270 | 270
[7 empty] | 17.5 |  |  | DEVIflex 18T 310W 230V 17.5m | 140F1401 | 35.4159 | 17.5 | 17.5 | 310 | 310
[7 empty] | 22 |  |  | DEVIflex 18T 395W 230V 22m | 140F1238 | 42.8216 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | DEVIflex 18T 535W 230V 29m | 140F1239 | 52.2865 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | DEVIflex 18T 615W 230V 34m | 140F1240 | 47.3052 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | DEVIflex 18T 680W 230V 37m | 140F1241 | 59.3457 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | DEVIflex 18T 820W 230V 44m | 140F1242 | 62.4281 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | DEVIflex 18T 935W 230V 52m | 140F1243 | 72.9463 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | DEVIflex 18T 1005W 230V 54m | 140F1410 | 68.9071 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | DEVIflex 18T 1075W 230V 59m | 140F1244 | 71.7261 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | DEVIflex 18T 1220W 230V 68m | 140F1245 | 85.3535 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | DEVIflex 18T 1340W 230V 74m | 140F1246 | 95.2464 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | DEVIflex 18T 1485W 230V 82m | 140F1247 | 94.8881 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | DEVIflex 18T 1625W 230V 90m | 140F1248 | 101.7635 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | DEVIflex 18T 1880W 230V 105m | 140F1249 | 124.4419 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | DEVIflex 18T 2135W 230V 118m | 140F1250 | 127.4416 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | DEVIflex 18T 2420W 230V 131m | 140F1251 | 147.1973 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | DEVIflex 18T 2775W 230V 155m | 140F1252 | 138.063 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | DEVIflex 18T 3050W 230V 170m | 140F1402 | 163.7246 | 170 | 170 | 3050 | 3050
DEVIsafe 20T, 230 V | DEVIsafe 20T 250W 230V 12m | 12 |  | 17 |  | 33 |  |  |  | DEVIsafe 20T | 0 | 0 |  | 0 |  | 0
|  | 36 | 1 | 34 | 0.94446 |  | 6 | 0.9167 |  | DEVIsafe 20T 125W 230V 6m | 140F1273 | 28.9254 | 6 | 6 | 125 | 125
|  |  | DEVIsafe 20T 250W 230V 12m |  | DEVIsafe 20T 335W 230V 17m |  | 12 | DEVIsafe 20T 675W 230V 33m | 140F1277 | DEVIsafe 20T 250W 230V 12m | 140F1274 | 39.2108 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.083303 |  | DEVIsafe 20T 335W 230V 17m | 140F1275 | 44.1423 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | DEVIsafe 20T 505W 230V 25m | 140F1276 | 51.718 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsafe 20T 675W 230V 33m | 140F1277 | 57.804 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | DEVIsafe 20T 830W 230V 42m | 140F1278 | 66.0327 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | DEVIsafe 20T 1000W 230V 50m | 140F1279 | 77.6812 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsafe 20T 1200W 230V 60m | 140F1280 | 89.9506 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | DEVIsafe 20T 1370W 230V 68m | 140F1281 | 97.1499 | 68 | 68 | 1370 | 1370
[7 empty] | 76 |  |  | DEVIsafe 20T 1545W 230V 76m | 140F1199 | 102.8038 | 76 | 76 | 1545 | 1545
[7 empty] | 85 |  |  | DEVIsafe 20T 1700W 230V 85m | 140F1282 | 109.215 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | DEVIsafe 20T 2040W 230V 101m | 140F1283 | 125.7509 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | DEVIsafe 20T 2360W 230V 118m | 140F1284 | 138.3392 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | DEVIsafe 20T 2685W 230V 135m | 140F1285 | 144.806 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | DEVIsafe 20T 3025W 230V 152m | 140F1286 | 157.0882 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | DEVIsafe 20T 3385W 230V 170m | 140F1287 | 174.0406 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | DEVIsafe 20T 3895W 230V 194m | 140F1288 | 190.3484 | 194 | 194 | 3895 | 3895
DEVIsnow 20T, 230 V | DEVIsnow 20T 250W 230V 12m | 12 |  | 17 |  | 33 |  |  |  | DEVIsnow 20T, 230 V | 0 |  |  | 0 |  | 0
|  | 36 | 1 | 34 | 0.94446 |  | 6 | 0.9167 |  | DEVIsnow 20T 125W 230V 6m | 140F1116 |  | 6 | 6 | 125 | 125
|  |  | DEVIsnow 20T 250W 230V 12m |  | DEVIsnow 20T 332W 230V 17m |  | 12 | DEVIsnow 20T 677W 230V 33m | 140F1118 | DEVIsnow 20T 250W 230V 12m | 83902100 |  | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.083303 |  | DEVIsnow 20T 332W 230V 17m | 140F1117 |  | 17 | 17 | 332 | 332
[7 empty] | 25 |  |  | DEVIsnow 20T 505W 230V 25m | 83902101 |  | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsnow 20T 677W 230V 33m | 140F1118 |  | 33 | 33 | 677 | 677
[7 empty] | 40 |  |  | DEVIsnow 20T 855W 230V 40m | 83902102 |  | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | DEVIsnow 20T 1000W 230V 50m | 83902103 |  | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsnow 20T 1200W 230V 60m | 83902104 |  | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | DEVIsnow 20T 1333W 230V 70m | 83902105 |  | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | DEVIsnow 20T 1695W 230V 85m | 83902106 |  | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | DEVIsnow 20T 2060W 230V 100m | 83902107 |  | 100 | 100 | 2060 | 2060
[7 empty] | 115 |  |  | DEVIsnow 20T 2421W 230V 115m | 140F1119 |  | 115 | 115 | 2421 | 2421
[7 empty] | 135 |  |  | DEVIsnow 20T 2685W 230V 135m | 83902108 |  | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | DEVIsnow 20T 3066W 230V 150m | 83902109 |  | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | DEVIsnow 20T 3382W 230V 170m | 83902110 |  | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | DEVIsnow 20T 3875W 230V 195m | 83902111 |  | 195 | 195 | 3875 | 3875
DEVIsnow 30T, 230 V | DEVIsnow 30T 1020W 230V 34m | 10 |  | 14 |  | 34 | 0 |  |  | DEVIsnow 30T, 230 V | 0 | 0 |  | 0 |  | 0
|  | 30 | 0.83334 | 28 | 0.7778 |  | 5 | 0.94447 |  | DEVIsnow 30T 150W 230V 5m | 89845995 | 27.7051 | 5 | 5 | 150 | 150
|  |  | DEVIsnow 30T 300W 230V 10m |  | DEVIsnow 30T 400W 230V 14m |  | 10 | DEVIsnow 30T 1020W 230V 34m | 89846008 | DEVIsnow 30T 300W 230V 10m | 89846000 | 47.6576 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.055526 |  | DEVIsnow 30T 400W 230V 14m | 89846002 | 53.3626 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | DEVIsnow 30T 630W 230V 20m | 89846004 | 61.8816 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | DEVIsnow 30T 830W 230V 27m | 89846006 | 71.4505 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | DEVIsnow 30T 1020W 230V 34m | 89846008 | 82.4261 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | DEVIsnow 30T 1250W 230V 40m | 89846010 | 90.9761 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | DEVIsnow 30T 1350W 230V 45m | 89846012 | 97.6812 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | DEVIsnow 30T 1440W 230V 50m | 89846014 | 106.9097 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | DEVIsnow 30T 1700W 230V 55m | 89846016 | 116.9281 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | DEVIsnow 30T 1860W 230V 63m | 89846018 | 128.1624 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | DEVIsnow 30T 2060W 230V 70m | 89846020 | 133.5726 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | DEVIsnow 30T 2340W 230V 78m | 89846022 | 145.3033 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | DEVIsnow 30T 2420W 230V 85m | 89846024 | 150.4317 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | DEVIsnow 30T 2930W 230V 95m | 89846026 | 160.1027 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | DEVIsnow 30T 3290W 230V 110m | 89846028 | 179.2554 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | DEVIsnow 30T 3680W 230V 125m | 89846030 | 188.7066 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | DEVIsnow 30T 4110W 230V 140m | 89846032 | 192.178 | 140 | 140 | 4110 | 4110
DEVIcomfort 10T, 230 V | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 10 |  | 10 |  | 28 | 0 |  |  | Set DEVIcomfort 10T W/double adhesive tape | 0 | 0 |  | 0 |  | 0
|  | 30 | 0.83334 | 20 | 0.55558 |  | 10 | 0.77781 |  | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 87101700 | 37.1175 | 10 | 10 | 100 | 100
|  |  | DEVIcomfort 10T 100W 230V 10m with double adhesive tape |  | DEVIcomfort 10T 100W 230V 10m with double adhesive tape |  | 20 | DEVIcomfort 10T 300W 230V 28m with double adhesive tape | 87101706 | DEVIcomfort 10T 200W 230V 20m with double adhesive tape | 87101702 | 39.3455 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.22219 |  | DEVIcomfort 10T 300W 230V 28m with double adhesive tape | 87101706 | 42.4788 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m with double adhesive tape | 87101708 | 55.8652 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m with double adhesive tape | 87101710 | 58.5378 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m with double adhesive tape | 87101712 | 71.8987 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m with double adhesive tape | 87101714 | 69.4793 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m with double adhesive tape | 87101716 | 86.3431 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m with double adhesive tape | 87101718 | 90.337 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m with double adhesive tape | 87101720 | 96.8938 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m with double adhesive tape | 87101722 | 102.8547 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m with double adhesive tape | 87101724 | 112.4678 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m with double adhesive tape | 87101728 | 139.6788 | 170 | 170 | 1700 | 1700
| DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 10 |  | 10 |  | 28 |  |  |  | Set DEVIcomfort 10T W/Flexpipe and endcap | 0 | 0 |  |  |  | 0
|  | 30 | 0.83334 | 20 | 0.55558 |  | 10 | 0.77781 |  | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101100 | 57.557 | 10 | 10 | 100 | 100
|  |  | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m |  | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m |  | 20 | DEVIcomfort 10T 300W 230V 28m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101104 | DEVIcomfort 10T 200W 230V 20m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101102 | 56.2081 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.22219 |  | DEVIcomfort 10T 300W 230V 28m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101104 | 68.2614 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101106 | 84.2502 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101108 | 100.2324 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101110 | 111.7354 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101112 | 129.5072 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101114 | 138.2771 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101116 | 148.0345 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101118 | 167.7854 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101120 | 198.9273 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101122 | 213.6489 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101124 | 246.4735 | 170 | 170 | 1700 | 1700
DEVIbasic 10S, 230 V | DEVIbasic 10S 299W 230V 30m | 0 |  | 0 |  | 30 |  |  |  | DEVIbasic 10S | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 21 | 0.83336 |  | DEVIbasic 10S 202W 230V 21m | 84001500 | 42.0258 | 21 | 21 | 202 | 202
|  |  | #N/A |  | #N/A |  | 26 | DEVIbasic 10S 299W 230V 30m | 84001510 | DEVIbasic 10S 268W 230V 26m | 84001505 | 31.1078 | 26 | 26 | 268 | 268
[7 empty] | 30 | 0.16664 |  | DEVIbasic 10S 299W 230V 30m | 84001510 | 41.096 | 30 | 30 | 299 | 299
[7 empty] | 37 |  |  | DEVIbasic 10S 376W 230V 37m | 84001515 | 36.0663 | 37 | 37 | 376 | 376
[7 empty] | 46 |  |  | DEVIbasic 10S 446W 230V 46m | 84001520 | 39.8957 | 46 | 46 | 446 | 446
[7 empty] | 50 |  |  | DEVIbasic 10S 501W 230V 50m | 84001525 | 40.4031 | 50 | 50 | 501 | 501
[7 empty] | 58 |  |  | DEVIbasic 10S 570W 230V 58m | 84001530 | 41.3 | 58 | 58 | 570 | 570
[7 empty] | 66 |  |  | DEVIbasic 10S 668W 230V 66m | 84001535 | 44.1354 | 66 | 66 | 668 | 668
[7 empty] | 77 |  |  | DEVIbasic 10S 763W 230V 77m | 84001540 | 50.942 | 77 | 77 | 763 | 763
[7 empty] | 90 |  |  | DEVIbasic 10S 904W 230V 90m | 84001545 | 48.2002 | 90 | 90 | 904 | 904
[7 empty] | 103 |  |  | DEVIbasic 10S 1027W 230V 103m | 84001550 | 53.7508 | 103 | 103 | 1027 | 1027
[7 empty] | 114 |  |  | DEVIbasic 10S 1133W 230V 114m | 84001555 | 59.6308 | 114 | 114 | 1133 | 1133
[7 empty] | 125 |  |  | DEVIbasic 10S 1245W 230V 125m | 84001560 | 73.5661 | 125 | 125 | 1245 | 1245
[7 empty] | 140 |  |  | DEVIbasic 10S 1400W 230V 140m | 84001565 | 76.5857 | 140 | 140 | 1400 | 1400
[7 empty] | 159 |  |  | DEVIbasic 10S 1584W 230V 159m | 84001570 | 84.2231 | 159 | 159 | 1584 | 1584
[7 empty] | 170 |  |  | DEVIbasic 10S 1707W 230V 170m | 84001575 | 106.6948 | 170 | 170 | 1707 | 1707
[7 empty] | 188 |  |  | DEVIbasic 10S 1876W 230V 188m | 84001580 | 108.3834 | 188 | 188 | 1876 | 1876
[7 empty] | 230 |  |  | DEVIbasic 10S 2300W 230V 230m | 84001585 | 179.3887 | 230 | 230 | 2300 | 2300
[7 empty] | 275 |  |  | DEVIbasic 10S 2741W 230V 275m | 84001590 | 237.7555 | 275 | 275 | 2741 | 2741
[7 empty] | 325 |  |  | DEVIbasic 10S 3245W 230V 325m | 84001595 | 253.4445 | 325 | 325 | 3245 | 3245
[7 empty] | 407 |  |  | DEVIbasic 10S 4069W 230V 407m | 84001600 | 322.5794 | 407 | 407 | 4069 | 4069
DEVIbasic 20S, 230 V | DEVIbasic 20S 375W 230V 18m | 9 |  | 18 |  | 32 |  |  |  | DEVIbasic 20S, 230 V | 0 | 0
|  | 27 | 0.75001 | 36 | 1 |  | 9 | 0.88892 |  | DEVIbasic 20S 170W 230V 9m | 140F0260 | 21.6338 | 9 | 9 | 170 | 170
|  |  | DEVIbasic 20S 170W 230V 9m |  | DEVIbasic 20S 375W 230V 18m |  | 14 | DEVIbasic 20S 640W 230V 32m | 140F0218 | DEVIbasic 20S 260W 230V 14m | 140F0215 | 24.4171 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.11108 |  | DEVIbasic 20S 375W 230V 18m | 140F0216 | 26.8774 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | DEVIbasic 20S 520W 230V 26m | 140F0217 | 32.1521 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | DEVIbasic 20S 640W 230V 32m | 140F0218 | 37.123 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | DEVIbasic 20S 800W 230V 39m | 140F0219 | 41.5959 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | DEVIbasic 20S 1070W 230V 53m | 140F0220 | 51.5364 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | DEVIbasic 20S 1260W 230V 63m | 140F0221 | 59.717 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | DEVIbasic 20S 1465W 230V 74m | 140F0222 | 71.7707 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | DEVIbasic 20S 1820W 230V 91m | 140F0223 | 85.0183 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | DEVIbasic 20S 2215W 230V 110m | 140F0224 | 102.2243 | 110 | 110 | 2215 | 2215
[7 empty] | 131 |  |  | DEVIbasic 20S 2640W 230V 131m | 140F0225 | 117.6106 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | DEVIbasic 20S 3170W 230V 159m | 140F0226 | 137.5381 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | DEVIbasic 20S 3855W 230V 192m | 140F0227 | 160.6359 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | DEVIbasic 20S 4565W 230V 228m | 140F0228 | 154.2219 | 228 | 228 | 4565 | 4565
[7 empty] | 56 |  |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 | 67.4779 | 56 | 56 | 1100 | 1100
[7 empty] | 69 |  |  | DEVIbasic 20S 1375W 400V 69m | 140F0230 | 74.5087 | 69 | 69 | 1375 | 1375
[7 empty] | 93 |  |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 | 121.6736 | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 | 150.2169 | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 | 169.5973 | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 | 160.3213 | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 | 187.3359 | 229 | 229 | 4575 | 4575
DEVIbasic 20S, 400 V | #N/A | 0 |  | 0 |  | 0 |  |  |  | DEVIbasic 20S, 400 V |  |  |  | 0
| 3e-05 | 0 | 1e-05 | 0 | 2e-05 |  | 56 | 3e-05 |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 |  | 56 | 56 | 1100 | 1100
|  |  | #N/A |  | #N/A |  | 69 | #N/A | #N/A | DEVIbasic 20S 1375W 400V 69m | 140F0230 |  | 69 | 69 | 1375 | 1375
[7 empty] | 93 | 0.99997 |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 |  | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 |  | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 |  | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 |  | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 |  | 229 | 229 | 4575 | 4575
ECflex 6T, 230 V | ECflex 6T 180W 230V 30m | 0 |  | 0 |  | 30 |  |  |  | ECflex 6T | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 30 | 0.83336 |  | ECflex 6T 180W 230V 30m | 088L6436 | 56.452 | 30 | 30 | 180 | 180
|  |  | #N/A |  | #N/A |  | 40 | ECflex 6T 180W 230V 30m | 088L6436 | ECflex 6T 250W 230V 40m | 088L6437 | 61.78 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.16664 |  | ECflex 6T 310W 230V 50m | 088L6438 | 0 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | ECflex 6T 345W 230V 60m | 088L6439 | 0 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | ECflex 6T 415W 230V 70m | 088L6440 | 95.73 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | ECflex 6T 500W 230V 80m | 088L6441 | 84.31 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | ECflex 6T 540W 230V 90m | 088L6442 | 0 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | ECflex 6T 635W 230V 100m | 088L6443 | 0 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | ECflex 6T 720W 230V 115m | 088L6444 | 115.97 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | ECflex 6T 770W 230V 129m | 088L6445 | 135.21 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | ECflex 6T 870W 230V 140m | 088L6446 | 0 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | ECflex 6T 915W 230V 160m | 088L6447 | 0 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | ECflex 6T 1095W 230V 180m | 088L6448 | 0 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | ECflex 6T 1160W 230V 190m | 088L6449 | 0 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | ECflex 6T 1260W 230V 200m | 088L6450 | 134.45 | 200 | 200 | 1260 | 1260
ECflex 10T, 230 V | ECflex 10T 365W 230V 35m | 10 |  | 15 |  | 35 |  |  |  | ECflex 10T | 0 | 0 |  | 0
|  | 30 | 0.83334 | 30 | 0.83335 |  | 2 | 0.97225 |  | ECflex 10T 20W 230V 2m | 088L6021 | 0 | 2 | 2 | 20 | 20
|  |  | ECflex 10T 100W 230V 10m |  | ECflex 10T 135W 230V 15m |  | 4 | ECflex 10T 365W 230V 35m | 088L6076 | ECflex 10T 40W 230V 4m | 088L6022 | 23.66 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.027748 |  | ECflex 10T 60W 230V 6m | 088L6023 | 23.675 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | ECflex 10T 80W 230V 8m | 088L6024 | 38.848 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | ECflex 10T 100W 230V 10m | 088L6025 | 35.7395 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | ECflex 10T 135W 230V 15m | 088L6074 | 33.3757 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | ECflex 10T 205W 230V 20m | 088L6026 | 55.0854 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | ECflex 10T 240W 230V 25m | 088L6075 | 31.1582 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | ECflex 10T 290W 230V 30m | 088L6027 | 64.9289 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | ECflex 10T 365W 230V 35m | 088L6076 | 39.4572 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | ECflex 10T 390W 230V 40m | 088L6028 | 72.2422 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | ECflex 10T 505W 230V 50m | 088L6029 | 81.8063 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | ECflex 10T 600W 230V 60m | 088L6030 | 101.6101 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | ECflex 10T 695W 230V 70m | 088L6031 | 79.21 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | ECflex 10T 795W 230V 80m | 088L6032 | 112.065 | 80 | 80 | 795 | 795
[7 empty] | 90 |  |  | ECflex 10T 920W 230V 90m | 088L6073 | 105.5445 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | ECflex 10T 990W 230V 100m | 088L6034 | 124.7212 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | ECflex 10T 1220W 230V 120m | 088L6035 | 155.1798 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | ECflex 10T 1410W 230V 140m | 088L6036 | 164.6128 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | ECflex 10T 1575W 230V 160m | 088L6077 | 128.7611 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | ECflex 10T 1760W 230V 180m | 088L6078 | 132.6395 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | ECflex 10T 1990W 230V 200m | 088L6079 | 163.5142 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | ECflex 10T 2050W 230V 210m | 088L6080 | 170.1106 | 210 | 210 | 2050 | 2050
ECflex 18T, 230 V | ECflex 18T 615W 230V 34m | 10 |  | 15 |  | 34 |  |  |  | ECflex 18T | 0 | 0 |  | 0
|  | 30 | 0.83334 | 30 | 0.83335 |  | 7.3 | 0.94447 |  | ECflex 18T 130W 230V 7,3m | 088L6037 | 29.5982 | 7,3 | 7.3 | 130 | 130
|  |  | ECflex 18T 180W 230V 10m |  | ECflex 18T 270W 230V 15m |  | 10 | ECflex 18T 615W 230V 34m | 088L6042 | ECflex 18T 180W 230V 10m | 088L6038 | 37.1244 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.055526 |  | ECflex 18T 230W 230V 12,8m | 088L6081 | 0 | 2,8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | ECflex 18T 270W 230V 15m | 088L6039 | 39.7327 | 15 | 15 | 270 | 270
[7 empty] | 7.5 |  |  | ECflex 18T 310W 230V 17,5m | 088L6082 | 45.79 | 7,5 | 7.5 | 310 | 310
[7 empty] | 22 |  |  | ECflex 18T 395W 230V 22m | 088L6040 | 43.2868 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | ECflex 18T 535W 230V 29m | 088L6041 | 51.0825 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | ECflex 18T 615W 230V 34m | 088L6042 | 56.3231 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | ECflex 18T 680W 230V 37m | 088L6043 | 61.1988 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | ECflex 18T 820W 230V 44m | 088L6044 | 66.18 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | ECflex 18T 935W 230V 52m | 088L6045 | 75.4182 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | ECflex 18T 1005W 230V 54m | 088L6083 | 115.765 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | ECflex 18T 1075W 230V 59m | 088L6046 | 76.8697 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | ECflex 18T 1220W 230V 68m | 088L6047 | 84.6495 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | ECflex 18T 1340W 230V 74m | 088L6048 | 89.1979 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | ECflex 18T 1485W 230V 82m | 088L6049 | 99.5225 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | ECflex 18T 1625W 230V 90m | 088L6050 | 101.0678 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | ECflex 18T 1880W 230V 105m | 088L6051 | 109.4646 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | ECflex 18T 2135W 230V 118m | 088L6052 | 117.1417 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | ECflex 18T 2420W 230V 131m | 088L6053 | 126.0686 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | ECflex 18T 2775W 230V 155m | 088L6054 | 143.8278 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | ECflex 18T 3050W 230V 170m | 088L6084 | 160.0119 | 170 | 170 | 3050 | 3050
ECflex 20T, 230 V | ECflex 20T 700W 230V 36m | 10 |  | 16.5 |  | 36 | 0 |  |  | ECflex 20T | 0 | 0 |  | 0
|  | 30 | 0.83334 | 33 | 0.91669 |  | 7.1 | 1 |  | ECflex 20T 140W 230V 7,1m | 088L6055 | 30.0769 | 7,1 | 7.1 | 140 | 140
|  |  | ECflex 20T 195W 230V 10m |  | ECflex 20T 330W 230V 16,5m |  | 10 | ECflex 20T 700W 230V 36m | 088L6061 | ECflex 20T 195W 230V 10m | 088L6056 | 34.7379 | 10 | 10 | 195 | 195
[7 empty] | 16.5 | 3e-05 |  | ECflex 20T 330W 230V 16,5m | 088L6057 | 40.2383 | 16,5 | 16.5 | 330 | 330
[7 empty] | 21 |  |  | ECflex 20T 415W 230V 21m | 088L6058 | 39.123 | 21 | 21 | 415 | 415
[7 empty] | 28 |  |  | ECflex 20T 555W 230V 28m | 088L6059 | 41.1882 | 28 | 28 | 555 | 555
[7 empty] | 32 |  |  | ECflex 20T 650W 230V 32m | 088L6060 | 40.9284 | 32 | 32 | 650 | 650
[7 empty] | 36 |  |  | ECflex 20T 700W 230V 36m | 088L6061 | 48.0644 | 36 | 36 | 700 | 700
[7 empty] | 43 |  |  | ECflex 20T 835W 230V 43m | 088L6062 | 53.9827 | 43 | 43 | 835 | 835
[7 empty] | 50 |  |  | ECflex 20T 970W 230V 50m | 088L6063 | 62.8224 | 50 | 50 | 970 | 970
[7 empty] | 56 |  |  | ECflex 20T 1130W 230V 56m | 088L6064 | 63.0011 | 56 | 56 | 1130 | 1130
[7 empty] | 65 |  |  | ECflex 20T 1275W 230V 65m | 088L6065 | 60.3244 | 65 | 65 | 1275 | 1275
[7 empty] | 70 |  |  | ECflex 20T 1415W 230V 70m | 088L6066 | 69.6247 | 70 | 70 | 1415 | 1415
[7 empty] | 78 |  |  | ECflex 20T 1565W 230V 78m | 088L6067 | 85.983 | 78 | 78 | 1565 | 1565
[7 empty] | 86 |  |  | ECflex 20T 1700W 230V 86m | 088L6068 | 88.4146 | 86 | 86 | 1700 | 1700
[7 empty] | 100 |  |  | ECflex 20T 1975W 230V 100m | 088L6069 | 91.5054 | 100 | 100 | 1975 | 1975
[7 empty] | 112 |  |  | ECflex 20T 2250W 230V 112m | 088L6070 | 94.6579 | 112 | 112 | 2250 | 2250
[7 empty] | 125 |  |  | ECflex 20T 2530W 230V 125m | 088L6071 | 106.6561 | 125 | 125 | 2530 | 2530
[7 empty] | 148 |  |  | ECflex 20T 2905W 230V 148m | 088L6072 | 104.4955 | 148 | 148 | 2905 | 2905
ECbasic 20S, 230 V | ECbasic 20S 375W 230V 18m | 9 |  | 18 |  | 32 | 0 |  |  | ECbasic 20S, 230 V | 0 | 0 |  | 0
|  | 27 | 0.75001 | 36 | 1 |  | 9 | 0.88892 |  | ECbasic 20S 170W 230V 9m | 088L2130 | 28.7912 | 9 | 9 | 170 | 170
|  |  | ECbasic 20S 170W 230V 9m |  | ECbasic 20S 375W 230V 18m |  | 14 | ECbasic 20S 640W 230V 32m | 088L2134 | ECbasic 20S 260W 230V 14m | 088L2131 | 33.2947 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.11108 |  | ECbasic 20S 375W 230V 18m | 088L2132 | 34.8516 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | ECbasic 20S 520W 230V 26m | 088L2133 | 38.1866 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | ECbasic 20S 640W 230V 32m | 088L2134 | 38.3272 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | ECbasic 20S 800W 230V 39m | 088L2135 | 46.3013 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | ECbasic 20S 1070W 230V 53m | 088L2136 | 55.6788 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | ECbasic 20S 1260W 230V 63m | 088L2137 | 63.4345 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | ECbasic 20S 1465W 230V 74m | 088L2138 | 68.8052 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | ECbasic 20S 1820W 230V 91m | 088L2139 | 79.3664 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | ECbasic 20S 2025W 230V 110m | 088L2140 | 93.4831 | 110 | 110 | 2025 | 2025
[7 empty] | 131 |  |  | ECbasic 20S 2640W 230V 131m | 088L2141 | 100.3531 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | ECbasic 20S 3170W 230V 159m | 088L2142 | 118.2952 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | ECbasic 20S 3855W 230V 192m | 088L2143 | 182.0267 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | ECbasic 20S 4565W 230V 228m | 088L2144 | 192.4472 | 228 | 228 | 4565 | 4565
ECsafe 20T, 230 V | ECsafe 20T 250W 230V 12m | 12 |  | 17 |  | 33 | 0 |  |  | ECsafe 20T, 230 V | 0 | 0 |  | 0
|  | 36 | 1 | 34 | 0.94446 |  | 6 | 0.9167 |  | ECsafe 20T 125W 230V 6m | 088L2170 | 40.081 | 6 | 6 | 125 | 125
|  |  | ECsafe 20T 250W 230V 12m |  | ECsafe 20T 335W 230V 17m |  | 12 | ECsafe 20T 675W 230V 33m | 088L2174 | ECsafe 20T 250W 230V 12m | 088L2171 | 31.9684 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.083303 |  | ECsafe 20T 335W 230V 17m | 088L2172 | 68.228 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | ECsafe 20T 505W 230V 25m | 088L2173 | 43.6554 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | ECsafe 20T 675W 230V 33m | 088L2174 | 76.9596 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | ECsafe 20T 830W 230V 42m | 088L2175 | 74.052 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | ECsafe 20T 1000W 230V 50m | 088L2176 | 91.4092 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsafe 20T 1200W 230V 60m | 088L2177 | 97.1683 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | ECsafe 20T 1370W 230V 68m | 088L2178 | 141.2821 | 68 | 68 | 1370 | 1370
[7 empty] | 85 |  |  | ECsafe 20T 1700W 230V 85m | 088L2179 | 108.6337 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | ECsafe 20T 2040W 230V 101m | 088L2180 | 151.7474 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | ECsafe 20T 2360W 230V 118m | 088L2181 | 170.2478 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | ECsafe 20T 2685W 230V 135m | 088L2182 | 143.5807 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | ECsafe 20T 3025W 230V 152m | 088L2183 | 212.4829 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | ECsafe 20T 3385W 230V 170m | 088L2184 | 173.5106 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | ECsafe 20T 3895W 230V 194m | 088L2185 | 197.8234 | 194 | 194 | 3895 | 3895
ECsnow 20T, 230 V | ECsnow 20T 250W 230V 12m | 12 |  | 12 |  | 25 | 0 |  |  | ECsnow 20T, 230 V | 0 | 0 |  | 0
|  | 36 | 1 | 24 | 0.66669 |  | 12 | 0.69447 |  | ECsnow 20T 250W 230V 12m | 088L0470 | 50.0246 | 12 | 12 | 250 | 250
|  |  | ECsnow 20T 250W 230V 12m |  | ECsnow 20T 250W 230V 12m |  | 25 | ECsnow 20T 505W 230V 25m | 088L0471 | ECsnow 20T 505W 230V 25m | 088L0471 | 75.545 | 25 | 25 | 505 | 505
[7 empty] | 40 | 0.30553 |  | ECsnow 20T 855W 230V 40m | 088L0472 | 70.278 | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | ECsnow 20T 1000W 230V 50m | 088L0473 | 102.9437 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsnow 20T 1200W 230V 60m | 088L0474 | 98.592 | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | ECsnow 20T 1333W 230V 70m | 088L0475 | 112.234 | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | ECsnow 20T 1695W 230V 85m | 088L0476 | 126.2978 | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | ECsnow 20T 2060W 230V 100m | 088L0477 | 140.0643 | 100 | 100 | 2060 | 2060
[7 empty] | 135 |  |  | ECsnow 20T 2685W 230V 135m | 088L0478 | 237.331 | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | ECsnow 20T 3066W 230V 150m | 088L0479 | 225.2117 | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | ECsnow 20T 3382W 230V 170m | 088L0480 | 240.192 | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | ECsnow 20T 3875W 230V 195m | 088L0481 | 268.514 | 195 | 195 | 3875 | 3875
ECsnow 20T, 400 V | ECsnow 20T 570W 400V 30m | 0 |  | 0 |  | 30 | 0 |  |  | ECsnow 20T, 400 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 21 | 0.83336 |  | ECsnow 20T 433W 400V 21m | 088L0482 | 0 | 21 | 21 | 433 | 433
|  |  | ECsnow 20T, 400 V |  | ECsnow 20T, 400 V |  | 30 | ECsnow 20T 570W 400V 30m | 088L0483 | ECsnow 20T 570W 400V 30m | 088L0483 | 127.31 | 30 | 30 | 570 | 570
[7 empty] | 43 | 0.16664 |  | ECsnow 20T 888W 400V 43m | 088L0484 | 0 | 43 | 43 | 888 | 888
[7 empty] | 58 |  |  | ECsnow 20T 1165W 400V 58m | 088L0485 | 149.93 | 58 | 58 | 1165 | 1165
[7 empty] | 72 |  |  | ECsnow 20T 1463W 400V 72m | 088L0486 | 173.05 | 72 | 72 | 1463 | 1463
[7 empty] | 85 |  |  | ECsnow 20T 1780W 400V 85m | 088L0487 | 0 | 85 | 85 | 1780 | 1780
[7 empty] | 105 |  |  | ECsnow 20T 2073W 400V 105m | 088L0488 | 0 | 105 | 105 | 2073 | 2073
[7 empty] | 135 |  |  | ECsnow 20T 2628W 400V 135m | 088L0489 | 261.5 | 135 | 135 | 2628 | 2628
[7 empty] | 150 |  |  | ECsnow 20T 2905W 400V 150m | 088L0490 | 0 | 150 | 150 | 2905 | 2905
[7 empty] | 170 |  |  | ECsnow 20T 3245W 400V 170m | 088L0491 | 0 | 170 | 170 | 3245 | 3245
[7 empty] | 205 |  |  | ECsnow 20T 4108W 400V 205m | 088L0492 | 565.7643 | 205 | 205 | 4108 | 4108
ECsnow 30T, 230 V | ECsnow 30T 1020W 230V 34m | 10 |  | 14 |  | 34 | 0 |  |  | ECsnow 30T, 230 V | 0 | 0 |  | 0
|  | 30 | 0.83334 | 28 | 0.7778 |  | 5 | 0.94447 |  | ECsnow 30T 150W 230V 5m | 088L0230 | 40.71 | 5 | 5 | 150 | 150
|  |  | ECsnow 30T 300W 230V 10m |  | ECsnow 30T 400W 230V 14m |  | 10 | ECsnow 30T 1020W 230V 34m | 088L0236 | ECsnow 30T 300W 230V 10m | 088L0232 | 43.6665 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.055526 |  | ECsnow 30T 400W 230V 14m | 088L0233 | 67.3094 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | ECsnow 30T 630W 230V 20m | 088L0234 | 59.9004 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | ECsnow 30T 830W 230V 27m | 088L0235 | 67.2721 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | ECsnow 30T 1020W 230V 34m | 088L0236 | 71.2763 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | ECsnow 30T 1250W 230V 40m | 088L0237 | 77.9237 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | ECsnow 30T 1350W 230V 45m | 088L0238 | 90.352 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | ECsnow 30T 1440W 230V 50m | 088L0239 | 98.2883 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | ECsnow 30T 1700W 230V 55m | 088L0240 | 111.0086 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | ECsnow 30T 1860W 230V 63m | 088L0241 | 177.5437 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | ECsnow 30T 2060W 230V 70m | 088L0242 | 126.05 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | ECsnow 30T 2340W 230V 78m | 088L0243 | 137.5029 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | ECsnow 30T 2420W 230V 85m | 088L0244 | 145.1914 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | ECsnow 30T 2930W 230V 95m | 088L0245 | 169.1264 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | ECsnow 30T 3290W 230V 110m | 088L0246 | 170.9941 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | ECsnow 30T 3680W 230V 125m | 088L0247 | 219.1243 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | ECsnow 30T 4110W 230V 140m | 088L0248 | 228.6538 | 140 | 140 | 4110 | 4110
ECsnow 30T, 400 V | ECsnow 30T 1090W 400V 35m | 8.5 |  | 17.5 |  | 35 | 0 |  |  | ECsnow 30T, 400 V | 0 | 0 |  | 0
|  | 25.5 | 0.70834 | 35 | 0.97224 |  | 8.5 | 0.97225 |  | ECsnow 30T 267W 400V 8,5m | 088L0231 | 0 | 8,5 | 8.5 | 267 | 267
|  |  | ECsnow 30T 267W 400V 8,5m |  | ECsnow 30T 520W 400V 17,5m |  | 17.5 | ECsnow 30T 1090W 400V 35m | 088L0131 | ECsnow 30T 520W 400V 17,5m | 088L0130 | 130.16 | 17,5 | 17.5 | 520 | 520
[7 empty] | 35 | 0.027748 |  | ECsnow 30T 1090W 400V 35m | 088L0131 | 167.13 | 35 | 35 | 1090 | 1090
[7 empty] | 70 |  |  | ECsnow 30T 2160W 400V 70m | 088L0132 | 0 | 70 | 70 | 2160 | 2160
[7 empty] | 110 |  |  | ECsnow 30T 3225W 400V 110m | 088L0133 | 287.0967 | 110 | 110 | 3225 | 3225
[7 empty] | 145 |  |  | ECsnow 30T 4295W 400V 145m | 088L0134 | 325.2089 | 145 | 145 | 4295 | 4295
[7 empty] | 170 |  |  | ECsnow 30T 4955W 400V 170m | 088L0135 | 377.2227 | 170 | 170 | 4955 | 4955
[7 empty] | 190 |  |  | ECsnow 30T 5770W 400V 190m | 088L0136 | 432.585 | 190 | 190 | 5770 | 5770
[7 empty] | 215 |  |  | ECsnow 30T 6470W 400V 215m | 088L0137 | 493.1996 | 215 | 215 | 6470 | 6470
ECfreeze 7,5T, 400 V | ECfreeze 7,5T 35m 400V 260W | 0 |  | 0 |  | 35 | 0 |  |  | ECfreeze 7,5T, 400 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 35 | 0.97225 |  | ECfreeze 7,5T 35m 400V 260W | 088L6300 | 70.62 | 35 | 35 | 35 | 35
|  |  | ECfreeze 7,5T, 400 V |  | ECfreeze 7,5T, 400 V |  | 48 | ECfreeze 7,5T 35m 400V 260W | 088L6300 | ECfreeze 7,5T 48m 400V 355W | 088L6301 | 94.07 | 48 | 48 | 48 | 48
[7 empty] | 71 | 0.027748 |  | ECfreeze 7,5T 71m 400V 540W | 088L6302 | 136.47 | 71 | 71 | 71 | 71
[7 empty] | 118 |  |  | ECfreeze 7,5T 118m 400V 890W | 088L6303 | 214.8767 | 118 | 118 | 118 | 118
[7 empty] | 142 |  |  | ECfreeze 7,5T 142m 400V 1065W | 088L6304 | 0 | 142 | 142 | 142 | 142
[7 empty] | 170 |  |  | ECfreeze 7,5T 170m 400V 1280W | 088L6305 | 278.04 | 170 | 170 | 170 | 170
[7 empty] | 217 |  |  | ECfreeze 7,5T 217m 400V 1635W | 088L6306 | 311.015 | 217 | 217 | 217 | 217
[7 empty] | 241 |  |  | ECfreeze 7,5T 241m 400V 1810W | 088L6307 | 469.2575 | 241 | 241 | 241 | 241
[7 empty] | 288 |  |  | ECfreeze 7,5T 288m 400V 2160W | 088L6308 | 401.76 | 288 | 288 | 288 | 288
[7 empty] | 382 |  |  | ECfreeze 7,5T 382m 400V 2870W | 088L6309 | 602.0573 | 382 | 382 | 382 | 382
[7 empty] | 431 |  |  | ECfreeze 7,5T 431m 400V 3230W | 088L6310 | 685.628 | 431 | 431 | 431 | 431
[7 empty] | 482 |  |  | ECfreeze 7,5T 482m 400V 3610W | 088L6311 | 669.5915 | 482 | 482 | 482 | 482
[7 empty] | 552 |  |  | ECfreeze 7,5T 552m 400V 4140W | 088L6312 | 859.0133 | 552 | 552 | 552 | 552
DEVIinline 17T, 230 V | DEVIinline 17T 600w 230V 34.7m | 8.9 |  | 13.8 |  | 34.7 |  |  |  | DEVIinline 17T | 0 | 0
|  | 26.7 | 0.74168 | 27.6 | 0.76669 |  | 8.9 | 0.96392 |  | DEVIinline 17T 150w 230V 8.9m | 140F0670 | 22.6336 | 8.9 | 8.9 | 150 | 150
|  |  | DEVIinline 17T 150w 230V 8.9m |  | DEVIinline 17T 220w 230V 13.8m |  | 13.8 | DEVIinline 17T 600w 230V 34.7m | 140F0675 | DEVIinline 17T 220w 230V 13.8m | 140F0671 | 29.4637 | 13.8 | 13.8 | 220 | 220
[7 empty] | 18.5 | 0.036081 |  | DEVIinline 17T 300w 230V 18.5m | 140F0672 | 35.2289 | 18.5 | 18.5 | 300 | 300
[7 empty] | 24.8 |  |  | DEVIinline 17T 400w 230V 24.8m | 140F0673 | 39.1685 | 24.8 | 24.8 | 400 | 400
[7 empty] | 31 |  |  | DEVIinline 17T 500w 230V 31m | 140F0674 | 41.6024 | 31 | 31 | 500 | 500
[7 empty] | 34.7 |  |  | DEVIinline 17T 600w 230V 34.7m | 140F0675 | 50.1831 | 34.7 | 34.7 | 600 | 600
[7 empty] | 40.6 |  |  | DEVIinline 17T 700w 230V 40.6m | 140F0676 | 51.75 | 40.6 | 40.6 | 700 | 700
[7 empty] | 49.4 |  |  | DEVIinline 17T 850w 230V 49.4m | 140F0677 | 60.8962 | 49.4 | 49.4 | 850 | 850
[7 empty] | 52 |  |  | DEVIinline 17T 884w 230V 52m | 140F0678 | 63.0429 | 52 | 52 | 884 | 884
[7 empty] | 58.1 |  |  | DEVIinline 17T 1000w 230V 58.1m | 140F0679 | 66.9593 | 58.1 | 58.1 | 1000 | 1000
[7 empty] | 68 |  |  | DEVIinline 17T 1156w 230V 68m | 140F0680 | 77.2147 | 68 | 68 | 1156 | 1156
[7 empty] | 72.7 |  |  | DEVIinline 17T 1250w 230V 72.7m | 140F0681 | 87.9433 | 72.7 | 72.7 | 1250 | 1250
[7 empty] | 87.3 |  |  | DEVIinline 17T 1500w 230V 87.3m | 140F0682 | 90.8188 | 87.3 | 87.3 | 1500 | 1500
[7 empty] | 99 |  |  | DEVIinline 17T 1700w 230V 99m | 140F0683 | 111.5161 | 99 | 99 | 1700 | 1700
[7 empty] | 110.7 |  |  | DEVIinline 17T 1900w 230V 110.7m | 140F0684 | 112.746 | 110.7 | 110.7 | 1900 | 1900
[7 empty] | 122.4 |  |  | DEVIinline 17T 2100w 230V 122.4m | 140F0685 | 118.1148 | 122.4 | 122.4 | 2100 | 2100
[7 empty] | 134.1 |  |  | DEVIinline 17T 2300w 230V 134.1m | 140F0686 | 122.5696 | 134.1 | 134.1 | 2300 | 2300
[7 empty] | 151.6 |  |  | DEVIinline 17T 2600w 230V 151.6m | 140F0687 | 133.7841 | 151.6 | 151.6 | 2600 | 2600
[7 empty] | 197 |  |  | DEVIinline 17T 3356w 230V 197m | 140F0688 | 167.0509 | 197 | 197 | 3356 | 3356

## Cables Frame (hidden)
|  | 3 |  | 2 |  | 1
|  | 3.8667 |  | 5.8 |  | 11.6 | m |  |  | Product name |  | NWP, Euro
DEVIflex 6T, 230 V | #N/A | 0 |  | 0 |  | 0 |  |  |  | DEVIflex 6T | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 30 | 3e-05 |  | DEVIflex 6T 180W 230V 30m | 140F1200 | 47.2513 | 30 | 30 | 180 | 180
|  |  | #N/A |  | #N/A |  | 40 | #N/A | #N/A | DEVIflex 6T 250W 230V 40m | 140F1201 | 57.5741 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.99997 |  | DEVIflex 6T 310W 230V 50m | 140F1202 | 56.8685 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | DEVIflex 6T 345W 230V 60m | 140F1203 | 67.5677 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | DEVIflex 6T 415W 230V 70m | 140F1204 | 74.3959 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | DEVIflex 6T 500W 230V 80m | 140F1205 | 90.3704 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | DEVIflex 6T 540W 230V 90m | 140F1206 | 89.0582 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | DEVIflex 6T 635W 230V 100m | 140F1207 | 99.4569 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | DEVIflex 6T 720W 230V 115m | 140F1208 | 106.49 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | DEVIflex 6T 770W 230V 129m | 140F1209 | 119.4648 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | DEVIflex 6T 870W 230V 140m | 140F1210 | 131.6305 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | DEVIflex 6T 915W 230V 160m | 140F1211 | 163.8981 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | DEVIflex 6T 1095W 230V 180m | 140F1212 | 183.8546 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | DEVIflex 6T 1160W 230V 190m | 140F1213 | 173.5159 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | DEVIflex 6T 1260W 230V 200m | 140F1214 | 188.2218 | 200 | 200 | 1260 | 1260
DEVIflex 10T, 230 V | DEVIflex 10T 100W 230V 10m | 2 |  | 4 |  | 10 | 0 |  |  | DEVIflex 10T | 0 | 0 |  | 0 |  | 0
|  | 6 | 0.51725 | 8 | 0.68968 |  | 2 | 0.8621 |  | DEVIflex 10T 20W 230V 2m | 140F1215 | 31.3109 | 2 | 2 | 20 | 20
|  |  | DEVIflex 10T 20W 230V 2m |  | DEVIflex 10T 40W 230V 4m |  | 4 | DEVIflex 10T 100W 230V 10m | 140F1219 | DEVIflex 10T 40W 230V 4m | 140F1216 | 33.2887 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.1379 |  | DEVIflex 10T 60W 230V 6m | 140F1217 | 35.3357 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | DEVIflex 10T 80W 230V 8m | 140F1218 | 37.0131 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | DEVIflex 10T 100W 230V 10m | 140F1219 | 36.6142 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | DEVIflex 10T 135W 230V 15m | 140F1407 | 42.4905 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | DEVIflex 10T 205W 230V 20m | 140F1220 | 43.4206 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | DEVIflex 10T 240W 230V 25m | 140F1408 | 50.0213 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | DEVIflex 10T 290W 230V 30m | 140F1221 | 52.2615 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | DEVIflex 10T 365W 230V 35m | 140F1409 | 57.4915 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | DEVIflex 10T 390W 230V 40m | 140F1222 | 61.3884 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | DEVIflex 10T 505W 230V 50m | 140F1223 | 73.761 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | DEVIflex 10T 600W 230V 60m | 140F1224 | 83.1366 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | DEVIflex 10T 695W 230V 70m | 140F1225 | 92.4731 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | DEVIflex 10T 790W 230V 80m | 140F1226 | 104.2358 | 80 | 80 | 790 | 790
[7 empty] | 90 |  |  | DEVIflex 10T 920W 230V 90m | 140F1227 | 109.1824 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | DEVIflex 10T 990W 230V 100m | 140F1228 | 123.8087 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | DEVIflex 10T 1220W 230V 120m | 140F1229 | 137.0674 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | DEVIflex 10T 1410W 230V 140m | 140F1230 | 161.5301 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | DEVIflex 10T 1575W 230V 160m | 140F1231 | 168.7374 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | DEVIflex 10T 1760W 230V 180m | 140F1232 | 177.3665 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | DEVIflex 10T 1990W 230V 200m | 140F1233 | 214.8776 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | DEVIflex 10T 2050W 230V 210m | 140F1234 | 206.4709 | 210 | 210 | 2050 | 2050
DEVIflex 18T, 230 V | DEVIflex 18T 180W 230V 10m | 2.8 |  | 2.8 |  | 10 | 0 |  |  | DEVIflex 18T | 0 | 0 |  | 0 |  | 0
|  | 8.4 | 0.72415 | 5.6 | 0.48278 |  | 7.3 | 0.8621 |  | DEVIflex 18T 130W 230V 7.3m | 140F1235 | 29.9305 | 7.3 | 7.3 | 130 | 130
|  |  | DEVIflex 18T 230W 230V 12.8m |  | DEVIflex 18T 230W 230V 12.8m |  | 10 | DEVIflex 18T 180W 230V 10m | 140F1236 | DEVIflex 18T 180W 230V 10m | 140F1236 | 32.7963 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.1379 |  | DEVIflex 18T 230W 230V 12.8m | 140F1400 | 31.6809 | 2.8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | DEVIflex 18T 270W 230V 15m | 140F1237 | 37.6402 | 15 | 15 | 270 | 270
[7 empty] | 17.5 |  |  | DEVIflex 18T 310W 230V 17.5m | 140F1401 | 35.4159 | 17.5 | 17.5 | 310 | 310
[7 empty] | 22 |  |  | DEVIflex 18T 395W 230V 22m | 140F1238 | 42.8216 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | DEVIflex 18T 535W 230V 29m | 140F1239 | 52.2865 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | DEVIflex 18T 615W 230V 34m | 140F1240 | 47.3052 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | DEVIflex 18T 680W 230V 37m | 140F1241 | 59.3457 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | DEVIflex 18T 820W 230V 44m | 140F1242 | 62.4281 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | DEVIflex 18T 935W 230V 52m | 140F1243 | 72.9463 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | DEVIflex 18T 1005W 230V 54m | 140F1410 | 68.9071 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | DEVIflex 18T 1075W 230V 59m | 140F1244 | 71.7261 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | DEVIflex 18T 1220W 230V 68m | 140F1245 | 85.3535 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | DEVIflex 18T 1340W 230V 74m | 140F1246 | 95.2464 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | DEVIflex 18T 1485W 230V 82m | 140F1247 | 94.8881 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | DEVIflex 18T 1625W 230V 90m | 140F1248 | 101.7635 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | DEVIflex 18T 1880W 230V 105m | 140F1249 | 124.4419 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | DEVIflex 18T 2135W 230V 118m | 140F1250 | 127.4416 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | DEVIflex 18T 2420W 230V 131m | 140F1251 | 147.1973 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | DEVIflex 18T 2775W 230V 155m | 140F1252 | 138.063 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | DEVIflex 18T 3050W 230V 170m | 140F1402 | 163.7246 | 170 | 170 | 3050 | 3050
DEVIsafe 20T, 230 V | DEVIsafe 20T 125W 230V 6m | 0 |  | 0 |  | 6 |  |  |  | DEVIsafe 20T | 0 | 0 |  | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 6 | 0.51727 |  | DEVIsafe 20T 125W 230V 6m | 140F1273 | 28.9254 | 6 | 6 | 125 | 125
|  |  | #N/A |  | #N/A |  | 12 | DEVIsafe 20T 125W 230V 6m | 140F1273 | DEVIsafe 20T 250W 230V 12m | 140F1274 | 39.2108 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.48273 |  | DEVIsafe 20T 335W 230V 17m | 140F1275 | 44.1423 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | DEVIsafe 20T 505W 230V 25m | 140F1276 | 51.718 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsafe 20T 675W 230V 33m | 140F1277 | 57.804 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | DEVIsafe 20T 830W 230V 42m | 140F1278 | 66.0327 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | DEVIsafe 20T 1000W 230V 50m | 140F1279 | 77.6812 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsafe 20T 1200W 230V 60m | 140F1280 | 89.9506 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | DEVIsafe 20T 1370W 230V 68m | 140F1281 | 97.1499 | 68 | 68 | 1370 | 1370
[7 empty] | 76 |  |  | DEVIsafe 20T 1545W 230V 76m | 140F1199 | 102.8038 | 76 | 76 | 1545 | 1545
[7 empty] | 85 |  |  | DEVIsafe 20T 1700W 230V 85m | 140F1282 | 109.215 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | DEVIsafe 20T 2040W 230V 101m | 140F1283 | 125.7509 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | DEVIsafe 20T 2360W 230V 118m | 140F1284 | 138.3392 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | DEVIsafe 20T 2685W 230V 135m | 140F1285 | 144.806 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | DEVIsafe 20T 3025W 230V 152m | 140F1286 | 157.0882 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | DEVIsafe 20T 3385W 230V 170m | 140F1287 | 174.0406 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | DEVIsafe 20T 3895W 230V 194m | 140F1288 | 190.3484 | 194 | 194 | 3895 | 3895
DEVIsnow 20T, 230 V | DEVIsnow 20T 125W 230V 6m | 0 |  | 0 |  | 6 |  |  |  | DEVIsnow 20T, 230 V | 0 |  |  | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 6 | 0.51727 |  | DEVIsnow 20T 125W 230V 6m | 140F1116 |  | 6 | 6 | 125 | 125
|  |  | #N/A |  | #N/A |  | 12 | DEVIsnow 20T 125W 230V 6m | 140F1116 | DEVIsnow 20T 250W 230V 12m | 83902100 |  | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.48273 |  | DEVIsnow 20T 332W 230V 17m | 140F1117 |  | 17 | 17 | 332 | 332
[7 empty] | 25 |  |  | DEVIsnow 20T 505W 230V 25m | 83902101 |  | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | DEVIsnow 20T 677W 230V 33m | 140F1118 |  | 33 | 33 | 677 | 677
[7 empty] | 40 |  |  | DEVIsnow 20T 855W 230V 40m | 83902102 |  | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | DEVIsnow 20T 1000W 230V 50m | 83902103 |  | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | DEVIsnow 20T 1200W 230V 60m | 83902104 |  | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | DEVIsnow 20T 1333W 230V 70m | 83902105 |  | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | DEVIsnow 20T 1695W 230V 85m | 83902106 |  | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | DEVIsnow 20T 2060W 230V 100m | 83902107 |  | 100 | 100 | 2060 | 2060
[7 empty] | 115 |  |  | DEVIsnow 20T 2421W 230V 115m | 140F1119 |  | 115 | 115 | 2421 | 2421
[7 empty] | 135 |  |  | DEVIsnow 20T 2685W 230V 135m | 83902108 |  | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | DEVIsnow 20T 3066W 230V 150m | 83902109 |  | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | DEVIsnow 20T 3382W 230V 170m | 83902110 |  | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | DEVIsnow 20T 3875W 230V 195m | 83902111 |  | 195 | 195 | 3875 | 3875
DEVIsnow 30T, 230 V | DEVIsnow 30T 300W 230V 10m | 0 |  | 5 |  | 10 | 0 |  |  | DEVIsnow 30T, 230 V | 0 | 0 |  | 0 |  | 0
|  | 0 | 1e-05 | 10 | 0.86209 |  | 5 | 0.8621 |  | DEVIsnow 30T 150W 230V 5m | 89845995 | 27.7051 | 5 | 5 | 150 | 150
|  |  | DEVIsnow 30T, 230 V |  | DEVIsnow 30T 150W 230V 5m |  | 10 | DEVIsnow 30T 300W 230V 10m | 89846000 | DEVIsnow 30T 300W 230V 10m | 89846000 | 47.6576 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.1379 |  | DEVIsnow 30T 400W 230V 14m | 89846002 | 53.3626 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | DEVIsnow 30T 630W 230V 20m | 89846004 | 61.8816 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | DEVIsnow 30T 830W 230V 27m | 89846006 | 71.4505 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | DEVIsnow 30T 1020W 230V 34m | 89846008 | 82.4261 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | DEVIsnow 30T 1250W 230V 40m | 89846010 | 90.9761 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | DEVIsnow 30T 1350W 230V 45m | 89846012 | 97.6812 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | DEVIsnow 30T 1440W 230V 50m | 89846014 | 106.9097 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | DEVIsnow 30T 1700W 230V 55m | 89846016 | 116.9281 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | DEVIsnow 30T 1860W 230V 63m | 89846018 | 128.1624 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | DEVIsnow 30T 2060W 230V 70m | 89846020 | 133.5726 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | DEVIsnow 30T 2340W 230V 78m | 89846022 | 145.3033 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | DEVIsnow 30T 2420W 230V 85m | 89846024 | 150.4317 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | DEVIsnow 30T 2930W 230V 95m | 89846026 | 160.1027 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | DEVIsnow 30T 3290W 230V 110m | 89846028 | 179.2554 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | DEVIsnow 30T 3680W 230V 125m | 89846030 | 188.7066 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | DEVIsnow 30T 4110W 230V 140m | 89846032 | 192.178 | 140 | 140 | 4110 | 4110
DEVIcomfort 10T, 230 V | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 0 |  | 0 |  | 10 | 0 |  |  | Set DEVIcomfort 10T W/double adhesive tape | 0 | 0 |  | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 10 | 0.8621 |  | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 87101700 | 37.1175 | 10 | 10 | 100 | 100
|  |  | Set DEVIcomfort 10T W/double adhesive tape |  | Set DEVIcomfort 10T W/double adhesive tape |  | 20 | DEVIcomfort 10T 100W 230V 10m with double adhesive tape | 87101700 | DEVIcomfort 10T 200W 230V 20m with double adhesive tape | 87101702 | 39.3455 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.1379 |  | DEVIcomfort 10T 300W 230V 28m with double adhesive tape | 87101706 | 42.4788 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m with double adhesive tape | 87101708 | 55.8652 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m with double adhesive tape | 87101710 | 58.5378 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m with double adhesive tape | 87101712 | 71.8987 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m with double adhesive tape | 87101714 | 69.4793 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m with double adhesive tape | 87101716 | 86.3431 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m with double adhesive tape | 87101718 | 90.337 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m with double adhesive tape | 87101720 | 96.8938 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m with double adhesive tape | 87101722 | 102.8547 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m with double adhesive tape | 87101724 | 112.4678 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m with double adhesive tape | 87101728 | 139.6788 | 170 | 170 | 1700 | 1700
| DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 0 |  | 0 |  | 10 |  |  |  | Set DEVIcomfort 10T W/Flexpipe and endcap | 0 | 0 |  |  |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 10 | 0.8621 |  | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101100 | 57.557 | 10 | 10 | 100 | 100
|  |  | #N/A |  | #N/A |  | 20 | DEVIcomfort 10T 100W 230V 10m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101100 | DEVIcomfort 10T 200W 230V 20m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101102 | 56.2081 | 20 | 20 | 200 | 200
[7 empty] | 28 | 0.1379 |  | DEVIcomfort 10T 300W 230V 28m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101104 | 68.2614 | 28 | 28 | 300 | 300
[7 empty] | 41 |  |  | DEVIcomfort 10T 400W 230V 41m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101106 | 84.2502 | 41 | 41 | 400 | 400
[7 empty] | 50 |  |  | DEVIcomfort 10T 500W 230V 50m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101108 | 100.2324 | 50 | 50 | 500 | 500
[7 empty] | 57 |  |  | DEVIcomfort 10T 600W 230V 57m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101110 | 111.7354 | 57 | 57 | 600 | 600
[7 empty] | 70 |  |  | DEVIcomfort 10T 700W 230V 70m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101112 | 129.5072 | 70 | 70 | 700 | 700
[7 empty] | 81 |  |  | DEVIcomfort 10T 800W 230V 81m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101114 | 138.2771 | 81 | 81 | 800 | 800
[7 empty] | 90 |  |  | DEVIcomfort 10T 900W 230V 90m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101116 | 148.0345 | 90 | 90 | 900 | 900
[7 empty] | 100 |  |  | DEVIcomfort 10T 1000W 230V 100m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101118 | 167.7854 | 100 | 100 | 1000 | 1000
[7 empty] | 129 |  |  | DEVIcomfort 10T 1250W 230V 129m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101120 | 198.9273 | 129 | 129 | 1250 | 1250
[7 empty] | 142 |  |  | DEVIcomfort 10T 1400W 230V 142m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101122 | 213.6489 | 142 | 142 | 1400 | 1400
[7 empty] | 170 |  |  | DEVIcomfort 10T 1700W 230V 170m + Flexpipe and endcap + Flexpipe transition + Wire sensor 3 m | 87101124 | 246.4735 | 170 | 170 | 1700 | 1700
DEVIbasic 10S, 230 V | #N/A | 0 |  | 0 |  | 0 |  |  |  | DEVIbasic 10S | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 21 | 3e-05 |  | DEVIbasic 10S 202W 230V 21m | 84001500 | 42.0258 | 21 | 21 | 202 | 202
|  |  | #N/A |  | #N/A |  | 26 | #N/A | #N/A | DEVIbasic 10S 268W 230V 26m | 84001505 | 31.1078 | 26 | 26 | 268 | 268
[7 empty] | 30 | 0.99997 |  | DEVIbasic 10S 299W 230V 30m | 84001510 | 41.096 | 30 | 30 | 299 | 299
[7 empty] | 37 |  |  | DEVIbasic 10S 376W 230V 37m | 84001515 | 36.0663 | 37 | 37 | 376 | 376
[7 empty] | 46 |  |  | DEVIbasic 10S 446W 230V 46m | 84001520 | 39.8957 | 46 | 46 | 446 | 446
[7 empty] | 50 |  |  | DEVIbasic 10S 501W 230V 50m | 84001525 | 40.4031 | 50 | 50 | 501 | 501
[7 empty] | 58 |  |  | DEVIbasic 10S 570W 230V 58m | 84001530 | 41.3 | 58 | 58 | 570 | 570
[7 empty] | 66 |  |  | DEVIbasic 10S 668W 230V 66m | 84001535 | 44.1354 | 66 | 66 | 668 | 668
[7 empty] | 77 |  |  | DEVIbasic 10S 763W 230V 77m | 84001540 | 50.942 | 77 | 77 | 763 | 763
[7 empty] | 90 |  |  | DEVIbasic 10S 904W 230V 90m | 84001545 | 48.2002 | 90 | 90 | 904 | 904
[7 empty] | 103 |  |  | DEVIbasic 10S 1027W 230V 103m | 84001550 | 53.7508 | 103 | 103 | 1027 | 1027
[7 empty] | 114 |  |  | DEVIbasic 10S 1133W 230V 114m | 84001555 | 59.6308 | 114 | 114 | 1133 | 1133
[7 empty] | 125 |  |  | DEVIbasic 10S 1245W 230V 125m | 84001560 | 73.5661 | 125 | 125 | 1245 | 1245
[7 empty] | 140 |  |  | DEVIbasic 10S 1400W 230V 140m | 84001565 | 76.5857 | 140 | 140 | 1400 | 1400
[7 empty] | 159 |  |  | DEVIbasic 10S 1584W 230V 159m | 84001570 | 84.2231 | 159 | 159 | 1584 | 1584
[7 empty] | 170 |  |  | DEVIbasic 10S 1707W 230V 170m | 84001575 | 106.6948 | 170 | 170 | 1707 | 1707
[7 empty] | 188 |  |  | DEVIbasic 10S 1876W 230V 188m | 84001580 | 108.3834 | 188 | 188 | 1876 | 1876
[7 empty] | 230 |  |  | DEVIbasic 10S 2300W 230V 230m | 84001585 | 179.3887 | 230 | 230 | 2300 | 2300
[7 empty] | 275 |  |  | DEVIbasic 10S 2741W 230V 275m | 84001590 | 237.7555 | 275 | 275 | 2741 | 2741
[7 empty] | 325 |  |  | DEVIbasic 10S 3245W 230V 325m | 84001595 | 253.4445 | 325 | 325 | 3245 | 3245
[7 empty] | 407 |  |  | DEVIbasic 10S 4069W 230V 407m | 84001600 | 322.5794 | 407 | 407 | 4069 | 4069
DEVIbasic 20S, 230 V | DEVIbasic 20S 170W 230V 9m | 0 |  | 0 |  | 9 |  |  |  | DEVIbasic 20S, 230 V | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 9 | 0.77589 |  | DEVIbasic 20S 170W 230V 9m | 140F0260 | 21.6338 | 9 | 9 | 170 | 170
|  |  | #N/A |  | #N/A |  | 14 | DEVIbasic 20S 170W 230V 9m | 140F0260 | DEVIbasic 20S 260W 230V 14m | 140F0215 | 24.4171 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.22411 |  | DEVIbasic 20S 375W 230V 18m | 140F0216 | 26.8774 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | DEVIbasic 20S 520W 230V 26m | 140F0217 | 32.1521 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | DEVIbasic 20S 640W 230V 32m | 140F0218 | 37.123 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | DEVIbasic 20S 800W 230V 39m | 140F0219 | 41.5959 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | DEVIbasic 20S 1070W 230V 53m | 140F0220 | 51.5364 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | DEVIbasic 20S 1260W 230V 63m | 140F0221 | 59.717 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | DEVIbasic 20S 1465W 230V 74m | 140F0222 | 71.7707 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | DEVIbasic 20S 1820W 230V 91m | 140F0223 | 85.0183 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | DEVIbasic 20S 2215W 230V 110m | 140F0224 | 102.2243 | 110 | 110 | 2215 | 2215
[7 empty] | 131 |  |  | DEVIbasic 20S 2640W 230V 131m | 140F0225 | 117.6106 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | DEVIbasic 20S 3170W 230V 159m | 140F0226 | 137.5381 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | DEVIbasic 20S 3855W 230V 192m | 140F0227 | 160.6359 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | DEVIbasic 20S 4565W 230V 228m | 140F0228 | 154.2219 | 228 | 228 | 4565 | 4565
[7 empty] | 56 |  |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 | 67.4779 | 56 | 56 | 1100 | 1100
[7 empty] | 69 |  |  | DEVIbasic 20S 1375W 400V 69m | 140F0230 | 74.5087 | 69 | 69 | 1375 | 1375
[7 empty] | 93 |  |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 | 121.6736 | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 | 150.2169 | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 | 169.5973 | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 | 160.3213 | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 | 187.3359 | 229 | 229 | 4575 | 4575
DEVIbasic 20S, 400 V | #N/A | 0 |  | 0 |  | 0 |  |  |  | DEVIbasic 20S, 400 V |  |  |  | 0
| 3e-05 | 0 | 1e-05 | 0 | 2e-05 |  | 56 | 3e-05 |  | DEVIbasic 20S 1100W 400V 56m | 140F0229 |  | 56 | 56 | 1100 | 1100
|  |  | #N/A |  | #N/A |  | 69 | #N/A | #N/A | DEVIbasic 20S 1375W 400V 69m | 140F0230 |  | 69 | 69 | 1375 | 1375
[7 empty] | 93 | 0.99997 |  | DEVIbasic 20S 1850W 400V 93m | 140F0231 |  | 93 | 93 | 1850 | 1850
[7 empty] | 126 |  |  | DEVIbasic 20S 2550W 400V 126m | 140F0232 |  | 126 | 126 | 2550 | 2550
[7 empty] | 158 |  |  | DEVIbasic 20S 3175W 400V 158m | 140F0233 |  | 158 | 158 | 3175 | 3175
[7 empty] | 192 |  |  | DEVIbasic 20S 3850W 400V 192m | 140F0234 |  | 192 | 192 | 3850 | 3850
[7 empty] | 229 |  |  | DEVIbasic 20S 4575W 400V 229m | 140F0235 |  | 229 | 229 | 4575 | 4575
ECflex 6T, 230 V | #N/A | 0 |  | 0 |  | 0 |  |  |  | ECflex 6T | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 30 | 3e-05 |  | ECflex 6T 180W 230V 30m | 088L6436 | 56.452 | 30 | 30 | 180 | 180
|  |  | #N/A |  | #N/A |  | 40 | #N/A | #N/A | ECflex 6T 250W 230V 40m | 088L6437 | 61.78 | 40 | 40 | 250 | 250
[7 empty] | 50 | 0.99997 |  | ECflex 6T 310W 230V 50m | 088L6438 | 0 | 50 | 50 | 310 | 310
[7 empty] | 60 |  |  | ECflex 6T 345W 230V 60m | 088L6439 | 0 | 60 | 60 | 345 | 345
[7 empty] | 70 |  |  | ECflex 6T 415W 230V 70m | 088L6440 | 95.73 | 70 | 70 | 415 | 415
[7 empty] | 80 |  |  | ECflex 6T 500W 230V 80m | 088L6441 | 84.31 | 80 | 80 | 500 | 500
[7 empty] | 90 |  |  | ECflex 6T 540W 230V 90m | 088L6442 | 0 | 90 | 90 | 540 | 540
[7 empty] | 100 |  |  | ECflex 6T 635W 230V 100m | 088L6443 | 0 | 100 | 100 | 635 | 635
[7 empty] | 115 |  |  | ECflex 6T 720W 230V 115m | 088L6444 | 115.97 | 115 | 115 | 720 | 720
[7 empty] | 129 |  |  | ECflex 6T 770W 230V 129m | 088L6445 | 135.21 | 129 | 129 | 770 | 770
[7 empty] | 140 |  |  | ECflex 6T 870W 230V 140m | 088L6446 | 0 | 140 | 140 | 870 | 870
[7 empty] | 160 |  |  | ECflex 6T 915W 230V 160m | 088L6447 | 0 | 160 | 160 | 915 | 915
[7 empty] | 180 |  |  | ECflex 6T 1095W 230V 180m | 088L6448 | 0 | 180 | 180 | 1095 | 1095
[7 empty] | 190 |  |  | ECflex 6T 1160W 230V 190m | 088L6449 | 0 | 190 | 190 | 1160 | 1160
[7 empty] | 200 |  |  | ECflex 6T 1260W 230V 200m | 088L6450 | 134.45 | 200 | 200 | 1260 | 1260
ECflex 10T, 230 V | ECflex 10T 100W 230V 10m | 2 |  | 4 |  | 10 |  |  |  | ECflex 10T | 0 | 0 |  | 0
|  | 6 | 0.51725 | 8 | 0.68968 |  | 2 | 0.8621 |  | ECflex 10T 20W 230V 2m | 088L6021 | 0 | 2 | 2 | 20 | 20
|  |  | ECflex 10T 20W 230V 2m |  | ECflex 10T 40W 230V 4m |  | 4 | ECflex 10T 100W 230V 10m | 088L6025 | ECflex 10T 40W 230V 4m | 088L6022 | 23.66 | 4 | 4 | 40 | 40
[7 empty] | 6 | 0.1379 |  | ECflex 10T 60W 230V 6m | 088L6023 | 23.675 | 6 | 6 | 60 | 60
[7 empty] | 8 |  |  | ECflex 10T 80W 230V 8m | 088L6024 | 38.848 | 8 | 8 | 80 | 80
[7 empty] | 10 |  |  | ECflex 10T 100W 230V 10m | 088L6025 | 35.7395 | 10 | 10 | 100 | 100
[7 empty] | 15 |  |  | ECflex 10T 135W 230V 15m | 088L6074 | 33.3757 | 15 | 15 | 135 | 135
[7 empty] | 20 |  |  | ECflex 10T 205W 230V 20m | 088L6026 | 55.0854 | 20 | 20 | 205 | 205
[7 empty] | 25 |  |  | ECflex 10T 240W 230V 25m | 088L6075 | 31.1582 | 25 | 25 | 240 | 240
[7 empty] | 30 |  |  | ECflex 10T 290W 230V 30m | 088L6027 | 64.9289 | 30 | 30 | 290 | 290
[7 empty] | 35 |  |  | ECflex 10T 365W 230V 35m | 088L6076 | 39.4572 | 35 | 35 | 365 | 365
[7 empty] | 40 |  |  | ECflex 10T 390W 230V 40m | 088L6028 | 72.2422 | 40 | 40 | 390 | 390
[7 empty] | 50 |  |  | ECflex 10T 505W 230V 50m | 088L6029 | 81.8063 | 50 | 50 | 505 | 505
[7 empty] | 60 |  |  | ECflex 10T 600W 230V 60m | 088L6030 | 101.6101 | 60 | 60 | 600 | 600
[7 empty] | 70 |  |  | ECflex 10T 695W 230V 70m | 088L6031 | 79.21 | 70 | 70 | 695 | 695
[7 empty] | 80 |  |  | ECflex 10T 795W 230V 80m | 088L6032 | 112.065 | 80 | 80 | 795 | 795
[7 empty] | 90 |  |  | ECflex 10T 920W 230V 90m | 088L6073 | 105.5445 | 90 | 90 | 920 | 920
[7 empty] | 100 |  |  | ECflex 10T 990W 230V 100m | 088L6034 | 124.7212 | 100 | 100 | 990 | 990
[7 empty] | 120 |  |  | ECflex 10T 1220W 230V 120m | 088L6035 | 155.1798 | 120 | 120 | 1220 | 1220
[7 empty] | 140 |  |  | ECflex 10T 1410W 230V 140m | 088L6036 | 164.6128 | 140 | 140 | 1410 | 1410
[7 empty] | 160 |  |  | ECflex 10T 1575W 230V 160m | 088L6077 | 128.7611 | 160 | 160 | 1575 | 1575
[7 empty] | 180 |  |  | ECflex 10T 1760W 230V 180m | 088L6078 | 132.6395 | 180 | 180 | 1760 | 1760
[7 empty] | 200 |  |  | ECflex 10T 1990W 230V 200m | 088L6079 | 163.5142 | 200 | 200 | 1990 | 1990
[7 empty] | 210 |  |  | ECflex 10T 2050W 230V 210m | 088L6080 | 170.1106 | 210 | 210 | 2050 | 2050
ECflex 18T, 230 V | ECflex 18T 180W 230V 10m | 2.8 |  | 2.8 |  | 10 |  |  |  | ECflex 18T | 0 | 0 |  | 0
|  | 8.4 | 0.72415 | 5.6 | 0.48278 |  | 7.3 | 0.8621 |  | ECflex 18T 130W 230V 7,3m | 088L6037 | 29.5982 | 7,3 | 7.3 | 130 | 130
|  |  | ECflex 18T 230W 230V 12,8m |  | ECflex 18T 230W 230V 12,8m |  | 10 | ECflex 18T 180W 230V 10m | 088L6038 | ECflex 18T 180W 230V 10m | 088L6038 | 37.1244 | 10 | 10 | 180 | 180
[7 empty] | 2.8 | 0.1379 |  | ECflex 18T 230W 230V 12,8m | 088L6081 | 0 | 2,8 | 2.8 | 230 | 230
[7 empty] | 15 |  |  | ECflex 18T 270W 230V 15m | 088L6039 | 39.7327 | 15 | 15 | 270 | 270
[7 empty] | 7.5 |  |  | ECflex 18T 310W 230V 17,5m | 088L6082 | 45.79 | 7,5 | 7.5 | 310 | 310
[7 empty] | 22 |  |  | ECflex 18T 395W 230V 22m | 088L6040 | 43.2868 | 22 | 22 | 395 | 395
[7 empty] | 29 |  |  | ECflex 18T 535W 230V 29m | 088L6041 | 51.0825 | 29 | 29 | 535 | 535
[7 empty] | 34 |  |  | ECflex 18T 615W 230V 34m | 088L6042 | 56.3231 | 34 | 34 | 615 | 615
[7 empty] | 37 |  |  | ECflex 18T 680W 230V 37m | 088L6043 | 61.1988 | 37 | 37 | 680 | 680
[7 empty] | 44 |  |  | ECflex 18T 820W 230V 44m | 088L6044 | 66.18 | 44 | 44 | 820 | 820
[7 empty] | 52 |  |  | ECflex 18T 935W 230V 52m | 088L6045 | 75.4182 | 52 | 52 | 935 | 935
[7 empty] | 54 |  |  | ECflex 18T 1005W 230V 54m | 088L6083 | 115.765 | 54 | 54 | 1005 | 1005
[7 empty] | 59 |  |  | ECflex 18T 1075W 230V 59m | 088L6046 | 76.8697 | 59 | 59 | 1075 | 1075
[7 empty] | 68 |  |  | ECflex 18T 1220W 230V 68m | 088L6047 | 84.6495 | 68 | 68 | 1220 | 1220
[7 empty] | 74 |  |  | ECflex 18T 1340W 230V 74m | 088L6048 | 89.1979 | 74 | 74 | 1340 | 1340
[7 empty] | 82 |  |  | ECflex 18T 1485W 230V 82m | 088L6049 | 99.5225 | 82 | 82 | 1485 | 1485
[7 empty] | 90 |  |  | ECflex 18T 1625W 230V 90m | 088L6050 | 101.0678 | 90 | 90 | 1625 | 1625
[7 empty] | 105 |  |  | ECflex 18T 1880W 230V 105m | 088L6051 | 109.4646 | 105 | 105 | 1880 | 1880
[7 empty] | 118 |  |  | ECflex 18T 2135W 230V 118m | 088L6052 | 117.1417 | 118 | 118 | 2135 | 2135
[7 empty] | 131 |  |  | ECflex 18T 2420W 230V 131m | 088L6053 | 126.0686 | 131 | 131 | 2420 | 2420
[7 empty] | 155 |  |  | ECflex 18T 2775W 230V 155m | 088L6054 | 143.8278 | 155 | 155 | 2775 | 2775
[7 empty] | 170 |  |  | ECflex 18T 3050W 230V 170m | 088L6084 | 160.0119 | 170 | 170 | 3050 | 3050
ECflex 20T, 230 V | ECflex 20T 195W 230V 10m | 0 |  | 0 |  | 10 | 0 |  |  | ECflex 20T | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 7.1 | 0.8621 |  | ECflex 20T 140W 230V 7,1m | 088L6055 | 30.0769 | 7,1 | 7.1 | 140 | 140
|  |  | ECflex 20T |  | ECflex 20T |  | 10 | ECflex 20T 195W 230V 10m | 088L6056 | ECflex 20T 195W 230V 10m | 088L6056 | 34.7379 | 10 | 10 | 195 | 195
[7 empty] | 16.5 | 0.1379 |  | ECflex 20T 330W 230V 16,5m | 088L6057 | 40.2383 | 16,5 | 16.5 | 330 | 330
[7 empty] | 21 |  |  | ECflex 20T 415W 230V 21m | 088L6058 | 39.123 | 21 | 21 | 415 | 415
[7 empty] | 28 |  |  | ECflex 20T 555W 230V 28m | 088L6059 | 41.1882 | 28 | 28 | 555 | 555
[7 empty] | 32 |  |  | ECflex 20T 650W 230V 32m | 088L6060 | 40.9284 | 32 | 32 | 650 | 650
[7 empty] | 36 |  |  | ECflex 20T 700W 230V 36m | 088L6061 | 48.0644 | 36 | 36 | 700 | 700
[7 empty] | 43 |  |  | ECflex 20T 835W 230V 43m | 088L6062 | 53.9827 | 43 | 43 | 835 | 835
[7 empty] | 50 |  |  | ECflex 20T 970W 230V 50m | 088L6063 | 62.8224 | 50 | 50 | 970 | 970
[7 empty] | 56 |  |  | ECflex 20T 1130W 230V 56m | 088L6064 | 63.0011 | 56 | 56 | 1130 | 1130
[7 empty] | 65 |  |  | ECflex 20T 1275W 230V 65m | 088L6065 | 60.3244 | 65 | 65 | 1275 | 1275
[7 empty] | 70 |  |  | ECflex 20T 1415W 230V 70m | 088L6066 | 69.6247 | 70 | 70 | 1415 | 1415
[7 empty] | 78 |  |  | ECflex 20T 1565W 230V 78m | 088L6067 | 85.983 | 78 | 78 | 1565 | 1565
[7 empty] | 86 |  |  | ECflex 20T 1700W 230V 86m | 088L6068 | 88.4146 | 86 | 86 | 1700 | 1700
[7 empty] | 100 |  |  | ECflex 20T 1975W 230V 100m | 088L6069 | 91.5054 | 100 | 100 | 1975 | 1975
[7 empty] | 112 |  |  | ECflex 20T 2250W 230V 112m | 088L6070 | 94.6579 | 112 | 112 | 2250 | 2250
[7 empty] | 125 |  |  | ECflex 20T 2530W 230V 125m | 088L6071 | 106.6561 | 125 | 125 | 2530 | 2530
[7 empty] | 148 |  |  | ECflex 20T 2905W 230V 148m | 088L6072 | 104.4955 | 148 | 148 | 2905 | 2905
ECbasic 20S, 230 V | ECbasic 20S 170W 230V 9m | 0 |  | 0 |  | 9 | 0 |  |  | ECbasic 20S, 230 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 9 | 0.77589 |  | ECbasic 20S 170W 230V 9m | 088L2130 | 28.7912 | 9 | 9 | 170 | 170
|  |  | ECbasic 20S, 230 V |  | ECbasic 20S, 230 V |  | 14 | ECbasic 20S 170W 230V 9m | 088L2130 | ECbasic 20S 260W 230V 14m | 088L2131 | 33.2947 | 14 | 14 | 260 | 260
[7 empty] | 18 | 0.22411 |  | ECbasic 20S 375W 230V 18m | 088L2132 | 34.8516 | 18 | 18 | 375 | 375
[7 empty] | 26 |  |  | ECbasic 20S 520W 230V 26m | 088L2133 | 38.1866 | 26 | 26 | 520 | 520
[7 empty] | 32 |  |  | ECbasic 20S 640W 230V 32m | 088L2134 | 38.3272 | 32 | 32 | 640 | 640
[7 empty] | 39 |  |  | ECbasic 20S 800W 230V 39m | 088L2135 | 46.3013 | 39 | 39 | 800 | 800
[7 empty] | 53 |  |  | ECbasic 20S 1070W 230V 53m | 088L2136 | 55.6788 | 53 | 53 | 1070 | 1070
[7 empty] | 63 |  |  | ECbasic 20S 1260W 230V 63m | 088L2137 | 63.4345 | 63 | 63 | 1260 | 1260
[7 empty] | 74 |  |  | ECbasic 20S 1465W 230V 74m | 088L2138 | 68.8052 | 74 | 74 | 1465 | 1465
[7 empty] | 91 |  |  | ECbasic 20S 1820W 230V 91m | 088L2139 | 79.3664 | 91 | 91 | 1820 | 1820
[7 empty] | 110 |  |  | ECbasic 20S 2025W 230V 110m | 088L2140 | 93.4831 | 110 | 110 | 2025 | 2025
[7 empty] | 131 |  |  | ECbasic 20S 2640W 230V 131m | 088L2141 | 100.3531 | 131 | 131 | 2640 | 2640
[7 empty] | 159 |  |  | ECbasic 20S 3170W 230V 159m | 088L2142 | 118.2952 | 159 | 159 | 3170 | 3170
[7 empty] | 192 |  |  | ECbasic 20S 3855W 230V 192m | 088L2143 | 182.0267 | 192 | 192 | 3855 | 3855
[7 empty] | 228 |  |  | ECbasic 20S 4565W 230V 228m | 088L2144 | 192.4472 | 228 | 228 | 4565 | 4565
ECsafe 20T, 230 V | ECsafe 20T 125W 230V 6m | 0 |  | 0 |  | 6 | 0 |  |  | ECsafe 20T, 230 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 6 | 0.51727 |  | ECsafe 20T 125W 230V 6m | 088L2170 | 40.081 | 6 | 6 | 125 | 125
|  |  | ECsafe 20T, 230 V |  | ECsafe 20T, 230 V |  | 12 | ECsafe 20T 125W 230V 6m | 088L2170 | ECsafe 20T 250W 230V 12m | 088L2171 | 31.9684 | 12 | 12 | 250 | 250
[7 empty] | 17 | 0.48273 |  | ECsafe 20T 335W 230V 17m | 088L2172 | 68.228 | 17 | 17 | 335 | 335
[7 empty] | 25 |  |  | ECsafe 20T 505W 230V 25m | 088L2173 | 43.6554 | 25 | 25 | 505 | 505
[7 empty] | 33 |  |  | ECsafe 20T 675W 230V 33m | 088L2174 | 76.9596 | 33 | 33 | 675 | 675
[7 empty] | 42 |  |  | ECsafe 20T 830W 230V 42m | 088L2175 | 74.052 | 42 | 42 | 830 | 830
[7 empty] | 50 |  |  | ECsafe 20T 1000W 230V 50m | 088L2176 | 91.4092 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsafe 20T 1200W 230V 60m | 088L2177 | 97.1683 | 60 | 60 | 1200 | 1200
[7 empty] | 68 |  |  | ECsafe 20T 1370W 230V 68m | 088L2178 | 141.2821 | 68 | 68 | 1370 | 1370
[7 empty] | 85 |  |  | ECsafe 20T 1700W 230V 85m | 088L2179 | 108.6337 | 85 | 85 | 1700 | 1700
[7 empty] | 101 |  |  | ECsafe 20T 2040W 230V 101m | 088L2180 | 151.7474 | 101 | 101 | 2040 | 2040
[7 empty] | 118 |  |  | ECsafe 20T 2360W 230V 118m | 088L2181 | 170.2478 | 118 | 118 | 2360 | 2360
[7 empty] | 135 |  |  | ECsafe 20T 2685W 230V 135m | 088L2182 | 143.5807 | 135 | 135 | 2685 | 2685
[7 empty] | 152 |  |  | ECsafe 20T 3025W 230V 152m | 088L2183 | 212.4829 | 152 | 152 | 3025 | 3025
[7 empty] | 170 |  |  | ECsafe 20T 3385W 230V 170m | 088L2184 | 173.5106 | 170 | 170 | 3385 | 3385
[7 empty] | 194 |  |  | ECsafe 20T 3895W 230V 194m | 088L2185 | 197.8234 | 194 | 194 | 3895 | 3895
ECsnow 20T, 230 V | ECsnow 20T, 230 V | 0 |  | 0 |  | 0 | 0 |  |  | ECsnow 20T, 230 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 12 | 3e-05 |  | ECsnow 20T 250W 230V 12m | 088L0470 | 50.0246 | 12 | 12 | 250 | 250
|  |  | ECsnow 20T, 230 V |  | ECsnow 20T, 230 V |  | 25 | ECsnow 20T, 230 V | #N/A | ECsnow 20T 505W 230V 25m | 088L0471 | 75.545 | 25 | 25 | 505 | 505
[7 empty] | 40 | 0.99997 |  | ECsnow 20T 855W 230V 40m | 088L0472 | 70.278 | 40 | 40 | 855 | 855
[7 empty] | 50 |  |  | ECsnow 20T 1000W 230V 50m | 088L0473 | 102.9437 | 50 | 50 | 1000 | 1000
[7 empty] | 60 |  |  | ECsnow 20T 1200W 230V 60m | 088L0474 | 98.592 | 60 | 60 | 1200 | 1200
[7 empty] | 70 |  |  | ECsnow 20T 1333W 230V 70m | 088L0475 | 112.234 | 70 | 70 | 1333 | 1333
[7 empty] | 85 |  |  | ECsnow 20T 1695W 230V 85m | 088L0476 | 126.2978 | 85 | 85 | 1695 | 1695
[7 empty] | 100 |  |  | ECsnow 20T 2060W 230V 100m | 088L0477 | 140.0643 | 100 | 100 | 2060 | 2060
[7 empty] | 135 |  |  | ECsnow 20T 2685W 230V 135m | 088L0478 | 237.331 | 135 | 135 | 2685 | 2685
[7 empty] | 150 |  |  | ECsnow 20T 3066W 230V 150m | 088L0479 | 225.2117 | 150 | 150 | 3066 | 3066
[7 empty] | 170 |  |  | ECsnow 20T 3382W 230V 170m | 088L0480 | 240.192 | 170 | 170 | 3382 | 3382
[7 empty] | 195 |  |  | ECsnow 20T 3875W 230V 195m | 088L0481 | 268.514 | 195 | 195 | 3875 | 3875
ECsnow 20T, 400 V | ECsnow 20T, 400 V | 0 |  | 0 |  | 0 | 0 |  |  | ECsnow 20T, 400 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 21 | 3e-05 |  | ECsnow 20T 433W 400V 21m | 088L0482 | 0 | 21 | 21 | 433 | 433
|  |  | ECsnow 20T, 400 V |  | ECsnow 20T, 400 V |  | 30 | ECsnow 20T, 400 V | #N/A | ECsnow 20T 570W 400V 30m | 088L0483 | 127.31 | 30 | 30 | 570 | 570
[7 empty] | 43 | 0.99997 |  | ECsnow 20T 888W 400V 43m | 088L0484 | 0 | 43 | 43 | 888 | 888
[7 empty] | 58 |  |  | ECsnow 20T 1165W 400V 58m | 088L0485 | 149.93 | 58 | 58 | 1165 | 1165
[7 empty] | 72 |  |  | ECsnow 20T 1463W 400V 72m | 088L0486 | 173.05 | 72 | 72 | 1463 | 1463
[7 empty] | 85 |  |  | ECsnow 20T 1780W 400V 85m | 088L0487 | 0 | 85 | 85 | 1780 | 1780
[7 empty] | 105 |  |  | ECsnow 20T 2073W 400V 105m | 088L0488 | 0 | 105 | 105 | 2073 | 2073
[7 empty] | 135 |  |  | ECsnow 20T 2628W 400V 135m | 088L0489 | 261.5 | 135 | 135 | 2628 | 2628
[7 empty] | 150 |  |  | ECsnow 20T 2905W 400V 150m | 088L0490 | 0 | 150 | 150 | 2905 | 2905
[7 empty] | 170 |  |  | ECsnow 20T 3245W 400V 170m | 088L0491 | 0 | 170 | 170 | 3245 | 3245
[7 empty] | 205 |  |  | ECsnow 20T 4108W 400V 205m | 088L0492 | 565.7643 | 205 | 205 | 4108 | 4108
ECsnow 30T, 230 V | ECsnow 30T 300W 230V 10m | 0 |  | 5 |  | 10 | 0 |  |  | ECsnow 30T, 230 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 10 | 0.86209 |  | 5 | 0.8621 |  | ECsnow 30T 150W 230V 5m | 088L0230 | 40.71 | 5 | 5 | 150 | 150
|  |  | ECsnow 30T, 230 V |  | ECsnow 30T 150W 230V 5m |  | 10 | ECsnow 30T 300W 230V 10m | 088L0232 | ECsnow 30T 300W 230V 10m | 088L0232 | 43.6665 | 10 | 10 | 300 | 300
[7 empty] | 14 | 0.1379 |  | ECsnow 30T 400W 230V 14m | 088L0233 | 67.3094 | 14 | 14 | 400 | 400
[7 empty] | 20 |  |  | ECsnow 30T 630W 230V 20m | 088L0234 | 59.9004 | 20 | 20 | 630 | 630
[7 empty] | 27 |  |  | ECsnow 30T 830W 230V 27m | 088L0235 | 67.2721 | 27 | 27 | 830 | 830
[7 empty] | 34 |  |  | ECsnow 30T 1020W 230V 34m | 088L0236 | 71.2763 | 34 | 34 | 1020 | 1020
[7 empty] | 40 |  |  | ECsnow 30T 1250W 230V 40m | 088L0237 | 77.9237 | 40 | 40 | 1250 | 1250
[7 empty] | 45 |  |  | ECsnow 30T 1350W 230V 45m | 088L0238 | 90.352 | 45 | 45 | 1350 | 1350
[7 empty] | 50 |  |  | ECsnow 30T 1440W 230V 50m | 088L0239 | 98.2883 | 50 | 50 | 1440 | 1440
[7 empty] | 55 |  |  | ECsnow 30T 1700W 230V 55m | 088L0240 | 111.0086 | 55 | 55 | 1700 | 1700
[7 empty] | 63 |  |  | ECsnow 30T 1860W 230V 63m | 088L0241 | 177.5437 | 63 | 63 | 1860 | 1860
[7 empty] | 70 |  |  | ECsnow 30T 2060W 230V 70m | 088L0242 | 126.05 | 70 | 70 | 2060 | 2060
[7 empty] | 78 |  |  | ECsnow 30T 2340W 230V 78m | 088L0243 | 137.5029 | 78 | 78 | 2340 | 2340
[7 empty] | 85 |  |  | ECsnow 30T 2420W 230V 85m | 088L0244 | 145.1914 | 85 | 85 | 2420 | 2420
[7 empty] | 95 |  |  | ECsnow 30T 2930W 230V 95m | 088L0245 | 169.1264 | 95 | 95 | 2930 | 2930
[7 empty] | 110 |  |  | ECsnow 30T 3290W 230V 110m | 088L0246 | 170.9941 | 110 | 110 | 3290 | 3290
[7 empty] | 125 |  |  | ECsnow 30T 3680W 230V 125m | 088L0247 | 219.1243 | 125 | 125 | 3680 | 3680
[7 empty] | 140 |  |  | ECsnow 30T 4110W 230V 140m | 088L0248 | 228.6538 | 140 | 140 | 4110 | 4110
ECsnow 30T, 400 V | ECsnow 30T 267W 400V 8,5m | 0 |  | 0 |  | 8.5 | 0 |  |  | ECsnow 30T, 400 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 8.5 | 0.73279 |  | ECsnow 30T 267W 400V 8,5m | 088L0231 | 0 | 8,5 | 8.5 | 267 | 267
|  |  | ECsnow 30T, 400 V |  | ECsnow 30T, 400 V |  | 17.5 | ECsnow 30T 267W 400V 8,5m | 088L0231 | ECsnow 30T 520W 400V 17,5m | 088L0130 | 130.16 | 17,5 | 17.5 | 520 | 520
[7 empty] | 35 | 0.26721 |  | ECsnow 30T 1090W 400V 35m | 088L0131 | 167.13 | 35 | 35 | 1090 | 1090
[7 empty] | 70 |  |  | ECsnow 30T 2160W 400V 70m | 088L0132 | 0 | 70 | 70 | 2160 | 2160
[7 empty] | 110 |  |  | ECsnow 30T 3225W 400V 110m | 088L0133 | 287.0967 | 110 | 110 | 3225 | 3225
[7 empty] | 145 |  |  | ECsnow 30T 4295W 400V 145m | 088L0134 | 325.2089 | 145 | 145 | 4295 | 4295
[7 empty] | 170 |  |  | ECsnow 30T 4955W 400V 170m | 088L0135 | 377.2227 | 170 | 170 | 4955 | 4955
[7 empty] | 190 |  |  | ECsnow 30T 5770W 400V 190m | 088L0136 | 432.585 | 190 | 190 | 5770 | 5770
[7 empty] | 215 |  |  | ECsnow 30T 6470W 400V 215m | 088L0137 | 493.1996 | 215 | 215 | 6470 | 6470
ECfreeze 7,5T, 400 V | ECfreeze 7,5T, 400 V | 0 |  | 0 |  | 0 | 0 |  |  | ECfreeze 7,5T, 400 V | 0 | 0 |  | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 35 | 3e-05 |  | ECfreeze 7,5T 35m 400V 260W | 088L6300 | 70.62 | 35 | 35 | 35 | 35
|  |  | ECfreeze 7,5T, 400 V |  | ECfreeze 7,5T, 400 V |  | 48 | ECfreeze 7,5T, 400 V | #N/A | ECfreeze 7,5T 48m 400V 355W | 088L6301 | 94.07 | 48 | 48 | 48 | 48
[7 empty] | 71 | 0.99997 |  | ECfreeze 7,5T 71m 400V 540W | 088L6302 | 136.47 | 71 | 71 | 71 | 71
[7 empty] | 118 |  |  | ECfreeze 7,5T 118m 400V 890W | 088L6303 | 214.8767 | 118 | 118 | 118 | 118
[7 empty] | 142 |  |  | ECfreeze 7,5T 142m 400V 1065W | 088L6304 | 0 | 142 | 142 | 142 | 142
[7 empty] | 170 |  |  | ECfreeze 7,5T 170m 400V 1280W | 088L6305 | 278.04 | 170 | 170 | 170 | 170
[7 empty] | 217 |  |  | ECfreeze 7,5T 217m 400V 1635W | 088L6306 | 311.015 | 217 | 217 | 217 | 217
[7 empty] | 241 |  |  | ECfreeze 7,5T 241m 400V 1810W | 088L6307 | 469.2575 | 241 | 241 | 241 | 241
[7 empty] | 288 |  |  | ECfreeze 7,5T 288m 400V 2160W | 088L6308 | 401.76 | 288 | 288 | 288 | 288
[7 empty] | 382 |  |  | ECfreeze 7,5T 382m 400V 2870W | 088L6309 | 602.0573 | 382 | 382 | 382 | 382
[7 empty] | 431 |  |  | ECfreeze 7,5T 431m 400V 3230W | 088L6310 | 685.628 | 431 | 431 | 431 | 431
[7 empty] | 482 |  |  | ECfreeze 7,5T 482m 400V 3610W | 088L6311 | 669.5915 | 482 | 482 | 482 | 482
[7 empty] | 552 |  |  | ECfreeze 7,5T 552m 400V 4140W | 088L6312 | 859.0133 | 552 | 552 | 552 | 552
DEVIinline 17T, 230 V | DEVIinline 17T 150w 230V 8.9m | 0 |  | 0 |  | 8.9 |  |  |  | DEVIinline 17T | 0 | 0
|  | 0 | 1e-05 | 0 | 2e-05 |  | 8.9 | 0.76727 |  | DEVIinline 17T 150w 230V 8.9m | 140F0670 | 22.6336 | 8.9 | 8.9 | 150 | 150
|  |  | #N/A |  | #N/A |  | 13.8 | DEVIinline 17T 150w 230V 8.9m | 140F0670 | DEVIinline 17T 220w 230V 13.8m | 140F0671 | 29.4637 | 13.8 | 13.8 | 220 | 220
[7 empty] | 18.5 | 0.23273 |  | DEVIinline 17T 300w 230V 18.5m | 140F0672 | 35.2289 | 18.5 | 18.5 | 300 | 300
[7 empty] | 24.8 |  |  | DEVIinline 17T 400w 230V 24.8m | 140F0673 | 39.1685 | 24.8 | 24.8 | 400 | 400
[7 empty] | 31 |  |  | DEVIinline 17T 500w 230V 31m | 140F0674 | 41.6024 | 31 | 31 | 500 | 500
[7 empty] | 34.7 |  |  | DEVIinline 17T 600w 230V 34.7m | 140F0675 | 50.1831 | 34.7 | 34.7 | 600 | 600
[7 empty] | 40.6 |  |  | DEVIinline 17T 700w 230V 40.6m | 140F0676 | 51.75 | 40.6 | 40.6 | 700 | 700
[7 empty] | 49.4 |  |  | DEVIinline 17T 850w 230V 49.4m | 140F0677 | 60.8962 | 49.4 | 49.4 | 850 | 850
[7 empty] | 52 |  |  | DEVIinline 17T 884w 230V 52m | 140F0678 | 63.0429 | 52 | 52 | 884 | 884
[7 empty] | 58.1 |  |  | DEVIinline 17T 1000w 230V 58.1m | 140F0679 | 66.9593 | 58.1 | 58.1 | 1000 | 1000
[7 empty] | 68 |  |  | DEVIinline 17T 1156w 230V 68m | 140F0680 | 77.2147 | 68 | 68 | 1156 | 1156
[7 empty] | 72.7 |  |  | DEVIinline 17T 1250w 230V 72.7m | 140F0681 | 87.9433 | 72.7 | 72.7 | 1250 | 1250
[7 empty] | 87.3 |  |  | DEVIinline 17T 1500w 230V 87.3m | 140F0682 | 90.8188 | 87.3 | 87.3 | 1500 | 1500
[7 empty] | 99 |  |  | DEVIinline 17T 1700w 230V 99m | 140F0683 | 111.5161 | 99 | 99 | 1700 | 1700
[7 empty] | 110.7 |  |  | DEVIinline 17T 1900w 230V 110.7m | 140F0684 | 112.746 | 110.7 | 110.7 | 1900 | 1900
[7 empty] | 122.4 |  |  | DEVIinline 17T 2100w 230V 122.4m | 140F0685 | 118.1148 | 122.4 | 122.4 | 2100 | 2100
[7 empty] | 134.1 |  |  | DEVIinline 17T 2300w 230V 134.1m | 140F0686 | 122.5696 | 134.1 | 134.1 | 2300 | 2300
[7 empty] | 151.6 |  |  | DEVIinline 17T 2600w 230V 151.6m | 140F0687 | 133.7841 | 151.6 | 151.6 | 2600 | 2600
[7 empty] | 197 |  |  | DEVIinline 17T 3356w 230V 197m | 140F0688 | 167.0509 | 197 | 197 | 3356 | 3356

## Sheet2 (hidden)
U
Table 1 |  |  |  | 220
Constant values |  |  |  | 230
Heat exchange coefficient, αout | 23 W/(m2·°C) |  |  | 240
Min temp. on suface, tsurf | 3 °C |  |  | 380
400
460
| 230 V |  | 220 | 240 | 208 | 400 V | 380 V |  |  | 20
DEVIflex 18T | 18 | W/m | 16.47 | 19.62 | 14.76 |  |  |  |  | 25
ECbasic 20S | 20 | W/m | 18.3 | 21.08 | 16.4 | 20 | 18.3 | 60.9956 |  | 30 |  | #REF!
ECsafe 20T | 20 | W/m | 18.3 | 21.08 | 16.4 | 20 | 18.3 |  |  | 35 |  | #REF!
DEVIbasic 20S | 20 | W/m | 18.3 | 21.08 | 16.4 | 20 | 18.3 | 22.8733 |  | 40 |  | #REF!
DEVIsafe 20T | 20 | W/m | 18.3 | 21.08 | 16.4 | 20 | 18.3 |  |  | 45 |  | #REF!
DEVIflex 20T | 20 | W/m | 18.3 | 21.08 | 16.4 |  |  |  |  | 50 |  | #REF!
ECsnow 30T | 30 | W/m | 27.45 | 32.7 | 24.6 | 30 | 27.45
ECasphalt 30T | 30 | W/m | 27.45 | 32.7 | 24.6 | 30 | 27.45
DEVIsnow 30T | 30 | W/m | 27.45 | 32.7 | 24.6 | 30 | 27.45 |  |  | 5 | 5
DEVIasphalt 30T | 30 | W/m | 27.45 | 32.7 | 24.6 | 30 | 27.45 |  |  | 7.5 | 7.5
DEVIsnow 300 | 300 | W/m2 | 274.5 | 327 | 246 | 300 | 274.5 | 360 |  | 10
DEVIasphalt 300 | 300 | W/m2 | 274.5 | 327 | 246 | 300 | 274.5
400
[16 empty] | Foundation | Floor | Frame
| 220 | 230 | 240 |  | 220 | 230 | 240 | DEVIreg™ 330 (-10 ... +10°C) | 140F1070 |  | DEVIreg™ 330 (-10 ... +10°C) | 140F1070 | DEVIfast™ Metal 5 m In box | 19808234 | 5 | 25 | 25 | 50
DEVIflex 6T, 230 V | 5.4896 | 6 | 6.5331 | DEVIflex 18T, 230 V | 16.4688 | 18 | 19.5992 | DEVIreg™ 330 (+5 ... +45°C) | 140F1072 |  | DEVIreg™ Multi | 140F1139 | DEVIfast™ Metal 25 m In box | 19808236 | 25
DEVIbasic 10S, 230 V | 9.1493 | 10 | 10.8885 | DEVIsafe 20T, 230 V | 18.2987 | 20 | 21.7769 | DEVIreg™ 610 | 140F1080 |  | ECtemp 330 (-10…+10°C) | 088L0444 | DEVIclip™ c-c, 10 m | 19805220 | 10
DEVIflex 10T, 230 V | 9.1493 | 10 | 10.8885 | DEVIsnow 20T, 230 V | 18.2987 | 20 | 21.7769 | DEVIreg™ Multi | 140F1139 |  |  |  | ECfast 5 m Metal In box | 088L1053 | 5
DEVIflex 18T, 230 V | 16.4688 | 18 | 19.5992 | DEVIsnow 30T, 230 V | 27.448 | 30 | 32.6654 | ECtemp 330 (-10…+10°C) | 088L0444 |  |  |  | ECfast 25 m Metal In box | 088L1054 | 25
DEVIbasic 20S, 400 V | 6.0386 | 6.6 | 7.1864 | DEVIbasic 20S, 230 V | 18.2987 | 20 | 21.7769 | ECtemp 330 (+5…+45°C) | 088L0445
ECfreeze 7,5T, 400 V |  |  |  | ECflex 18T, 230 V | 16.4688 | 18 | 19.5992 | ECtemp 610 | 088L0448 |  |  |  | Tape aluminium 38 mm x 50 m | 19805076 | 50
|  |  |  | ECflex 20T, 230 V | 18.2987 | 20 | 21.7769 | [5 empty] | Tape aluminium 25 mm x 25 m | 19805078 | 25
|  |  |  | ECbasic 20S, 230 V | 18.2987 | 20 | 21.7769
|  |  |  | ECsafe 20T, 230 V | 18.2987 | 20 | 21.7769
|  |  |  | ECsnow 20T, 230 V | 18.2987 | 20 | 21.7769 | air room | 20
|  |  |  | ECsnow 30T, 230 V | 27.448 | 30 | 32.6654 | floor surf. | 28
p = a * (Tf - Tr)
| 230 | 220 | 240 | 400 | 380 | 460
DEVIflex 6T, 230 V | 6 | 5.4896 | 6.5331 | Not available for this voltage | Not available for this voltage | Not available for this voltage |  | Heat exchange coefficient, α1 | 8.7 | W/(m2*K) | (8,7 - 11)
DEVIflex 10T, 230 V | 10 | 9.1493 | 10.8885 | Not available for this voltage | Not available for this voltage | Not available for this voltage |  | p | 300 | W/m2
DEVIflex 18T, 230 V | 18 | 16.4688 | 19.5992 | Not available for this voltage | Not available for this voltage | Not available for this voltage |  | Tr | -30 | °C
DEVIbasic 10S, 230 V | 10 | 9.1493 | 10.8885 | Not available for this voltage | Not available for this voltage | Not available for this voltage
DEVIbasic 20S, 400 V | 6.6125 | 6.05 | 7.2 | 20 | 18.05 | 26.45 |  | Tf | 4.4828 | °C
ECflex 6T, 230 V | 6 | 5.4896 | 6.5331 | Not available for this voltage | Not available for this voltage | Not available for this voltage
ECflex 10T, 230 V | 10 | 9.1493 | 10.8885 | Not available for this voltage | Not available for this voltage | Not available for this voltage
ECflex 18T, 230 V | 18 | 16.4688 | 19.5992 | Not available for this voltage | Not available for this voltage | Not available for this voltage
ECflex 20T, 230 V | 20 | 18.2987 | 21.7769 | Not available for this voltage | Not available for this voltage | Not available for this voltage
ECbasic 20S, 230 V | 20 | 18.2987 | 21.7769 | Not available for this voltage | Not available for this voltage | Not available for this voltage
ECfreeze 7,5T, 400 V | Not available for this voltage | Not available for this voltage | Not available for this voltage | 7.5 | 6.7688 | 9.9188
DEVIflex 6T, 230 V | 6 |  | DEVIflex 6T, 230 V | DEVIbasic 20S, 400 V
DEVIflex 10T, 230 V | 10 |  | DEVIflex 10T, 230 V | ECfreeze 7,5T, 400 V
DEVIflex 18T, 230 V | 18 |  | DEVIflex 18T, 230 V
DEVIbasic 10S, 230 V | 10 |  | DEVIbasic 10S, 230 V
DEVIbasic 20S, 400 V | 20 |  | DEVIbasic 20S, 400 V
ECflex 6T, 230 V | 6 |  | ECflex 6T, 230 V
ECflex 10T, 230 V | 10 |  | ECflex 10T, 230 V
ECflex 18T, 230 V | 18 |  | ECflex 18T, 230 V
ECflex 20T, 230 V | 20 |  | ECflex 20T, 230 V
ECbasic 20S, 230 V | 20 |  | ECbasic 20S, 230 V
ECfreeze 7,5T, 400 V | 7.5

## Sheet3 (hidden)
23018 | 230 | 18 | 360 | 240 |  |  | _18_w
23020 | 230 | 20 | 400 | 266.6667 |  |  | _20_w
23030 | 230 | 30 | 600 | 400 | 300 | 240 | _30_w
230300 | 230 | 300 |  |  | 300 |  | _300_w
22016,47 | 220 | 16.47 | 329.4 | 219.6 |  |  | _16_47_w
22018,3 | 220 | 18.3 | 366 | 244 |  |  | _18_3_w
22027,45 | 220 | 27.45 | 549 | 366 | 274.5 | 219.6 | _27_45_w
220274,5 | 220 | 274.5 |  |  | 274.5 |  | _274_5_w
24019,62 | 240 | 19.62 | 392.4 | 261.6 |  |  | _19_62_w
24021,08 | 240 | 21.08 | 436 | 290.6667 |  |  | _21_08_w
24032,7 | 240 | 32.7 | 654 | 436 | 327 | 261.6 | _32_7_w
240327 | 240 | 327 |  |  | 327 |  | _327_w
20814,76 | 208 | 14.76 | 295.2 | 196.8 |  |  | _14_76_w
20816,4 | 208 | 16.4 | 328 | 218.6667 |  |  | _16_4_w
20824,6 | 208 | 24.6 | 492 | 328 | 246 | 196.8 | _24_6_w
208246 | 208 | 246 |  |  | 246 |  | _246_w
40018 | 400 | 18 | 360 | 240 |  |  | _18_w
40020 | 400 | 20 | 400 | 266.6667 |  |  | _20_w
40030 | 400 | 30 | 600 | 400 | 300 | 240 | _30_w
400300 | 400 | 300 |  |  | 300 |  | _300_w
38016,47 | 380 | 16.47 | 329.4 | 219.6 |  |  | _16_47_w
38018,3 | 380 | 18.3 | 366 | 244 |  |  | _18_3_w
38027,45 | 380 | 27.45 | 549 | 366 | 274.5 | 219.6 | _27_45_w
380274,5 | 380 | 274.5 |  |  | 274.5 |  | _274_5_w