## Straight line installation
0.36009
Heat loss calculation of pipeline and heating system selection
Evaluative calculation |  |  |  | Informational data (for more information see Application manual)
Cells with gray color - for data entry
Object data
| Length of pipe | 10 | m
| Outside pipe diameter, d | 50 | mm
| Insulation thickness, h | 25 | mm
| Thermal conductivity of insulation, λ | 0.05 | W/(m·°C)
| Desired temp, tu | 5 | °C
| Min outside temp, to | -10 | °C
| Voltage | 220 | V
| Safety factor | 1.3 | recommended 1,3
| Type of pipe | Plastic
System Calculation
| Heat loss, q (with safety factor) | 8.8336 | W/m
| Select cable type | Self-limiting cable
| DEVIpipeguard 25 | 24.5317 | W/m @ 5 °C
| Number of cable lines on pipe | 1
| Number of valves, flanges,etc. | 0 | pcs.
| Calculated cable length | 10 | m
| Calculated total output | 245.3166 | W
| Alutape, fixing element | 20 | m
| Control system | DEVIreg™ 330 (-10 ... +10°C)
Important to know
Note 1. For plastic pipes the linear output of resistive heating cables should not exceed 10 W/m. This restriction does not apply to self-limiting cables (SLC).
Note 2. If a voltage of 220 V, use the coefficient 0,915 for cable output.
Note 3. Apply aluminum tape below (mandatory for plastic pipes) and on top on the whole length of the cable.
| Note 4. Installing the thermostat is recommended. |  |  |  | Technical support: EH@danfoss.com
Note on C15: Drop-down list
Note on C17: Drop-down list
Note on C22: Drop-down list
Note on B23: Drop-down list
Note on C29: Drop-down list

## Spiral installation
0.95131
Heat loss calculation of pipeline and heating system selection
Evaluative calculation |  |  |  | Informational data (for more information see Application manual)
Cells with gray color - for data entry
Object data
| Length of pipe | 1 | m
| Outside pipe diameter, d | 20 | mm
| Insulation thickness, h | 10 | mm
| Thermal conductivity of insulation, λ | 0.035 | W/(m·°C)
| Desired temp, tu | 50 | °C
| Min outside temp, to | 25 | °C
| Voltage | 230 | V
| Safety factor | 1.2 | recommended 1,3
| Type of pipe | Metal
System Calculation
| Heat loss, Q (with safety factor) | 9.5131 | W
| Select cable type | Resistive cable
| DEVIcomfort 10T | 10 | W/m
| Required cable length | 1 | m
| Centre-centre distance for cables wrapped in a spiral, C-C | Use INLINE installation | cm
| Number of valves, flanges,etc. | 0 | pcs.
| Calculated cable length | 1 | m
| Calculated total output | 10 | W
| Alutape, fixing element | 1 | m
| Control system | DEVIreg™ 330 (+5 ... +45°C)
Important to know
Note 1. For plastic pipes the linear output of resistive heating cables should not exceed 10 W/m. This restriction does not apply to self-limiting cables (SLC).
Note 2. If a voltage of 220 V, use the coefficient 0,915 for cable output.
Note 3. Apply aluminum tape below (mandatory for plastic pipes) and on top on the whole length of the cable.
| Note 4. Installing the thermostat is recommended. |  |  |  | Technical support: EH@danfoss.com
Note on C15: Drop-down list
Note on C17: Drop-down list
Note on C22: Drop-down list
Note on B23: Drop-down list
Note on C31: Drop-down list

## Sheet2 (hidden)
Table 1
Pipe diameters
Inside pipe diameter | inch (NPS*) | 1/2 | 3/4 | 1 | 1 1/4" | 1 1/2 | 2 | 2 1/2 | 3 | 3 1/2 | 4 | 4 1/2 | 5 | 6 | 8 | 10 | 12
| mm (DN*) | 15 | 20 | 25 | 32 | 40 | 50 | 65 | 80 | 90 | 100 | 115 | 125 | 150 | 200 | 250 | 300
Outside pipe diameter**, mm |  | 21 | 27 | 34 | 42 | 48 | 60 | 73 | 89 | 102 | 114 | 127 | 141 | 168 | 219 | 273 | 324
* NPS - Nominal Pipe Size, DN - Diameter Nominal
** Approx. value for steel pipes
| Resistive cable | [8 empty] | U
| Self-limiting cable | [8 empty] | 220 | [7 empty] | U1 | 230 | V
[10 empty] | 230 | [7 empty] | U2 | 24 | V
| Metal | [8 empty] | 240 | [7 empty] | P1 | 33 | W/m
| Plastic | [16 empty] | P2 | 0.35932 | W/m
DEVIreg™ 330 (+5 ... +45°C)
DEVIreg™ 330 (-10 ... +10°C)
DEVIreg™ 330 (60 -160 °C)
DEVIreg™ 610
DEVIreg™ 130
DEVIreg™ Multi

## Sheet3 (hidden)
Table 2
Output of heating cables at 230/400 V
Factory manufacturer | Resistive heating cable
| 6 W/m | 10 W/m | 18 W/m | 20 W/m | 9 W/m
DEVI | DEVIflexTM 6T | DEVIflexTM 10T, DEVIbasicTM 10S, DEVIcomfortTM 10T | DEVIflexTM 18T | DEVIflexTM 20T, DEVIbasicTM 20S | DEVIaquaTM 9T
Factory manufacturer | Self-limiting heating cable
| 10 W/m @ 10 °C | 25 W/m @ 10 °C | 33 W/m @ 10 °C | 7 W/m @ 45 °C | 9 W/m @ 55 °C | 12 W/m @ 70 °C
DEVI | DEVIpipeguardTM 10, DEVIpipeheatTM 10 | DEVIpipeguardTM 25 | DEVIpipeguardTM 33 | DEVIhotwattTM 45 | DEVIhotwattTM 55 | DEVIhotwattTM 70
Note. If a voltage of 220 V, use the coefficient 0,915 for cable output
230
DEVIaqua 9T | 9 | W/m |  | DEVIpipeheat 10 | 10.8929 | W/m (@ 10 °C) | DEVIaqua 9T | 9 | W/m
DEVIflex 6T | 6 | W/m |  | DEVIpipeguard 10 | 10.8333 | W/m (@ 10 °C) | DEVIflex 6T | 6 | W/m
DEVIflex 10T | 10 | W/m |  | DEVIpipeguard 25 | 26.8125 | W/m (@ 10 °C) | DEVIflex 10T | 10 | W/m
DEVIflex 18T | 18 | W/m |  | DEVIpipeguard 33 | 35.25 | W/m (@ 10 °C) | DEVIbasic 10S | 10 | W/m
DEVIflex 20T | 20 | W/m |  | DEVIhotwatt 45 | 12.3333 | W/m (@ 45 °C) | DEVIcomfort 10T | 10 | W/m
DEVIbasic 10S | 10 | W/m |  | DEVIhotwatt 55 | 14 | W/m (@ 55 °C)
DEVIbasic 20S | 20 | W/m |  | DEVIhotwatt 70 | 21.75 | W/m (@ 70 °C)
DEVIcomfort 10T | 10 | W/m |  | DEVIpipeguard 30 Industry | 30.625 | W/m (@ 10 °C)
|  |  |  | DEVIpipeguard 60 Industry | 61.25 | W/m (@ 10 °C)
220
DEVIaqua 9T | 8.2344 | W/m |  | DEVIpipeheat 10 | 9.9662 | W/m (@ 10 °C) | DEVIaqua 9T | 8.2344 | W/m
DEVIflex 6T | 5.4896 | W/m |  | DEVIpipeguard 10 | 9.9118 | W/m (@ 10 °C) | DEVIflex 6T | 5.4896 | W/m
DEVIflex 10T | 9.1493 | W/m |  | DEVIpipeguard 25 | 24.5317 | W/m (@ 10 °C) | DEVIflex 10T | 9.1493 | W/m
DEVIflex 18T | 16.4688 | W/m |  | DEVIpipeguard 33 | 32.2514 | W/m (@ 10 °C) | DEVIbasic 10S | 9.1493 | W/m
DEVIflex 20T | 18.2987 | W/m |  | DEVIhotwatt 45 | 11.2842 | W/m (@ 45 °C) | DEVIcomfort 10T | 9.1493 | W/m
DEVIbasic 10S | 9.1493 | W/m |  | DEVIhotwatt 55 | 12.8091 | W/m (@ 55 °C)
DEVIbasic 20S | 18.2987 | W/m |  | DEVIhotwatt 70 | 19.8998 | W/m (@ 70 °C)
DEVIcomfort 10T | 9.1493 | W/m |  | DEVIpipeguard 30 Industry | 28.0198 | W/m (@ 10 °C)
|  |  |  | DEVIpipeguard 60 Industry | 56.0397 | W/m (@ 10 °C)
240
DEVIaqua 9T | 9.7996 | W/m |  | DEVIpipeheat 10 | 11.8607 | W/m (@ 10 °C) | DEVIaqua 9T | 9.7996 | W/m
DEVIflex 6T | 6.5331 | W/m |  | DEVIpipeguard 10 | 11.7958 | W/m (@ 10 °C) | DEVIflex 6T | 6.5331 | W/m
DEVIflex 10T | 10.8885 | W/m |  | DEVIpipeguard 25 | 29.1947 | W/m (@ 10 °C) | DEVIflex 10T | 10.8885 | W/m
DEVIflex 18T | 19.5992 | W/m |  | DEVIpipeguard 33 | 38.3819 | W/m (@ 10 °C) | DEVIbasic 10S | 10.8885 | W/m
DEVIflex 20T | 21.7769 | W/m |  | DEVIhotwatt 45 | 13.4291 | W/m (@ 45 °C) | DEVIcomfort 10T | 10.8885 | W/m
DEVIbasic 10S | 10.8885 | W/m |  | DEVIhotwatt 55 | 15.2439 | W/m (@ 55 °C)
DEVIbasic 20S | 21.7769 | W/m |  | DEVIhotwatt 70 | 23.6824 | W/m (@ 70 °C)
DEVIcomfort 10T | 10.8885 | W/m |  | DEVIpipeguard 30 Industry | 33.3459 | W/m (@ 10 °C)
|  |  |  | DEVIpipeguard 60 Industry | 66.6919 | W/m (@ 10 °C)

## Sheet4 (hidden)
1
2
3
4
Choose cable with higher W/m