## Roof
Roof application. Frost protection
Preliminary calculation of heat losses on the roofs and in the gutters and downpipes |  |  |  | Informational data (for more information see Application manual)
Cells with gray color - for data entry
Object data
| Desing temperature, tout | -5 | °C
| Level of roof insulation | Well insulated roof
| Voltage | 230 | V
| Length of gutter | 12 | m
| Length of down pipe | 10 | m
| Gutter/pipe diameter | 120 | mm
| Gutter valley area | 0 | m2
| Roof area | 15.5 | m2
System calculation
| Select cable type | Resistive cable
| DEVIsnow™ 30T | 30 | W/m
| Recommended heat density for roof edge and gutter valley | 230 | W/m2
| C-C distance for roof edge and gutter valley | 13.0435 | cm
| Number of cable lines in gutters and downpipes, n | 1 | Units
| Calculated cable length for roof edge | 118.8333 | m
| Calculated cable length for gutter valley | 0 | m
| Total output for roof edge | 3565 | W
| Total output for gutter valley | 0 | W
| Calculated cable length for gutter | 12 | m
| Calculated cable length for downpipe | 11 | m
| Total output for gutter | 360 | W
| Total output for downpipe | 330 | W
Control system
| Sensor parameters | Air temperature below +3 °C and moisture
| Thermostat | DEVIreg™ 850, Max 2x15 A (3450 W) @ 230 V
Important to know
Note 1. It is recommended to design output for ice and snow melting systems with maximum possible level.
Note 2. 2 lines of 30 W/m require minimum Ø120 mm downpipe.
Note 3. For a voltage of 220 V, use the coefficient 0,915.
Note 4. DEVIfast is recommended to use for cable fixing (C-C steps 2,5 cm). For copper roofs use DEVIfast Copper.
Note 5. For downpipes use DEVIfast Double Special RB for resistive cable, DEVIfast Double SLC RB for self-limiting cable.
| Note 6. Installing the thermostat is recommended. |  |  |  | Technical support: EH@danfoss.com

## Sheet3
Table 1
Recommended output (230/400 V)
Area | Cold roof | Hot roof | Max. rating | Cable rating
Valley gutter, roof surface | 200-300 W/m2 | 250-350 W/m2 | 400 W/m2 | 20-30 W/m
Downpipes, plastic roof gutters | 30-60 W/m | 40-60 W/m | 60 W/m | 20-30 W/m
Downpipes, metal roof gutters | 30-60 W/m | 40-60 W/m | 100 W/m | 20-30 W/m
Downpipes, wooden roof gutters | 30-40 W/m | 40 W/m | 40 W/m | 20 W/m
Table 2
Heat density, W/m2 (230/400 V)
[5 empty] | C-C distance, cm | DEVIiceguardTM 18 | DEVIsnowTM 20T, DEVIsafeTM 20T | DEVIsnowTM 30T
[6 empty] | 18 W/m @ 0 °C | 20 W/m | 30 W/m
[5 empty] | 5 | 360 | 400 | 600
[5 empty] | 7.5 | 240 | 266.6667 | 400
[5 empty] | 10 |  |  | 300
[5 empty] | 12.5 |  |  | 240
Note. If a voltage of 220 V, use the coefficient 0,915 for cable output
[9 empty] | 230V |  |  | 220V
[9 empty] | DEVIsafe™ 20T | 20 | W/m | DEVIsafe™ 20T | 18.3 | W/m
Resistive cable |  | U |  | DEVIreg™ 330 (60 -160 °C) |  |  |  |  | DEVIsnow™ 20T | 20 | W/m | DEVIsnow™ 20T | 18.3 | W/m
Self-limiting cable |  | 220 |  | DEVIreg™ 316 |  |  |  |  | DEVIsnow™ 30T | 30 | W/m | DEVIsnow™ 30T | 27.45 | W/m
|  | 230 |  | DEVIreg™ 850 |  |  |  |  | DEVIiceguard™ 18 (T) | 20 | W/m @ 0 °C | DEVIiceguard™ 18 (T) | 18.3 | W/m @ 0 °C
|  | 380 | [6 empty] | DEVIiceguard™ 18 (B) | 18 | W/m @ 0 °C | DEVIiceguard™ 18 (B) | 16.47 | W/m @ 0 °C
400
https://www.youtube.com/watch?v=rUgW65pIYqo
Well insulated roof
|  | Bad insulated roof |  |  |  | Air temperature below +3 °C
Air temperature between +3 °C and -7 °C
|  | 75 |  |  |  | Air temperature below +3 °C and moisture
100
120
150
200